## Лист1
No.: | Date | Refernce (Lot, Document, chapter,page) | Issue | Question Bidder | Answer Employer
1 | 2015-10-20 | "ICB_4 Substations_HVEN_04.09.15.pdf" Page 295/1036 Chapter 1.1.2.7.1 (General) | Training | “Training for overhead lines” We will not be responsible for OHLs. We assume not to do related training. | Trainings should be Implemeted regarding all equipment installed in substations during the reconstruction
2 | 2015-10-20 | "ICB_4 Substations_HVEN_04.09.15.pdf" Page 349/1036 (Vanadzo-1) | Trafo repair | Requirement: two (2) Transformers 110/10 kV 40 MVA to rehabilitate; two (2) Transformers 110/6 kV 40 MVA to rehabilitate; For evaluation of current transformer conditions we need the following: - Manufacturer - - Manufacturer- / commissioning date- - technical data (rating plate)- - PD-measurement / analyze - - oil in gas analysis - - failure suffered by the transformer- | Attached enclosed the rating name plates of transformers to be rehabilitated.
3 | 2015-10-20 | "ICB_4 Substations_HVEN_04.09.15.pdf" Page 377/1036 (Ashnak) | Trafo repair | Requirement: one (1) Autotransformer 220/110/10 kV 63 MVA to repair; two (2) Boost transformers 10/10 kV 40 MVA to repair; Repairing and painting with anti-corrosion paint of existing House transformers 10/0.4 kV 630 kVA; For evaluation of current transformer conditions we need the following: ՝ - Manufacturer - - Manufacturer- / commissioning date- - technical data (rating plate)- - PD-measurement / analyze - - oil in gas analysis - - failure suffered by the transformer- | Attached enclosed the rating name plates of transformers to be rehabilitated.
4 | 2015-10-20 | General question / all lots | Drawings | In order to do proper determination of scope and to find the best technical solution we need following as build drawings from existing substations: 1. Building - 2. Drainage / sewerage system- 3. Cable routes- 4. Layouts, sections- 5. Foundation plan- We need from the layouts / sections the workable files *.dwg for example or other format in order to implement new equipment. | I propose to use the existing layouts of substations which are included in Appendices after page 1035.
5 | 2015-10-20 | General question / all lots | Workable docs | We need for tender preparation we need following documents in workable files: 1. Price lists as *.xls - | As per WB requirments bidding document has been prepared in PDF ans MS Word formats.
6 | 2015-10-20 | General question / all lots | Tender docs in Armenian | Please send us the tender documentation in Armenian. - | It is already sent
7 | 2015-10-20 | "ICB_4 Substations_HVEN_04.09.15.pdf" Page 476/1036 Data sheet 110 kV disconnector | Operating device 110 kV disconnector | Operating device for 110 kV disconnector "single pole" requested. Could we offer instead of "single pole" "three pole" devices - means one drive for all three poles? In substations Vanadzor-1 and Allaverdi-2 three pole devices are installed. Devices will be cheaper and cabling also. | Yes, you can implement three pole operating devices
8 | 2015-10-20 | General question / all lots | Soil investigation | For the existing substations we need the soil investigation reports. | Soil investigations and expertizing should be Implemented by the Contractor as per technical documentation.
….
…
200 |  | ITB, clause 2.3 and Section IX, Contract Forms, Appendix 1 | Payment | According to ITB, clause 2.3 and Section IX, Contract Forms, Appendix 1, Payment Procedures and Contract Agreement Form, Clause 2.2 payments shall be effected as follows: (i) For advance payment and for Plant and Equipment supplied from within the Employer’s Country. Design Services and Installation Services shall be made by direct disbursement from the World Bank, and (ii) For Plant and Mandatory Spare Parts supplied from Abroad shall be made our through a confirmed irrevocable divisible documentary Letter of Credit to be opened by the Employer under the World bank Special Commitment Procedure in favour of the Contractor. All charges for the opening of the confirmed Letter of Credit are to be borne by the Employer. Please confirm if our understanding is correct or advice. | Yes, your understanding is correct
201 |  | Section IX, Contract Forms, Appendix 1 | Bonds | According to Section IX, Contract Forms, Appendix 1, Payment Procedures last paragraph is stated that “ The Contractor shall instruct its bank to issue and advance payment security made available to the Contractor in a bank in the country of the Employer”. The wording is not understandable. Advance Payment Securities or Performance Bonds provided by a foreign Contractor shall be issued by a First Class Bank of Contractor’s home country and advance Payment Securities or performance Bonds provide by a local Contractor to be issued by a bank in the country of the Employer. Please confirm. | In this regards we discuss with WB. As we will receive their reply we will inform you.
202 |  | ITB, Bid Data Sheet, Particular conditions | Price adjustment | We have noted, that according to the ITB/Bid Data Sheet and Bidding Forms, Price Adjustment, the prices of the price schedule 1, price schedule 2 and price schedule 4 shall be subject to adjustment during the performance of the contract as per the Price Adjustment Formula. Please confirm if our understanding is correct or advice. | Yes, your understanding is correct