## Лист1
# | Topic | Question | Reply
1 | As per SLD (Appendix 10 -110kV Charentsavan-3 substation single line diagram Ц to realize): | - 110kV voltage transformers (Item 1.1.1.8 - Supply of 110kV Voltage transformer (1-p)including necessary steel structure, cabling and earthing - 19 pcs) - as per SLD - 14 pcs. (3pcs X 3pole + 3pcs X 1-pole + 1pcs X 2-pole=9+3+2) Where is mistake and which version is correct? | The quantity of voltage transformers should be 19 pcs (4pcs X 3pole + 1 pcs X 1-pole + 1 pcs X 3 pole=12+1+6 = 19 pcs)
2 | As per SLD (Appendix 25 -110kV Vanadzor-1 substation single line diagram Ц to realize): | - 110 kV Circuit breackers (Item 1.1.1.1 - Supply of 110 kV Circuit breackers (3-p) including necessary steel structure, cabling and earthing - 3 pcs) - as per SLD - 6 pcs. Where is mistake and which version is correct? - 110 kV Disconectors (Item 1.1.1.2 - Supply of 110 kV Disconectors with motor driver (3-p) + 1 earthing switch including necessary steel structure, cabling and earthing - 5 pcs) - as per SLD 8 pcs. Where is mistake and which version is correct? - 110 kV Disconectors (Item 1.1.1.3 - Supply of 110 kV Disconectors with motor driver (3-p) + 2 earthing switch including necessary steel structure, cabling and earthing - 2 pcs) - as per SLD 3 pcs. Where is mistake and which version is correct? - 110 kV Disconectors (Item 1.1.1.4 - Supply of 110 kV Disconectors with motor driver (3-p)including necessary steel structure, cabling and earthing - 3 pcs) - as per SLD 6 pcs. Where is mistake and which version is correct? - 110 kV Surge arresters (Item 1.1.1.6 - Supply of 110 kV Surge arresters (1-p) including necessary steel structure, cabling and earthing - 12 pcs) - as per SLD 18pcs. Where is mistake and which version is correct? - 110 kV Surge arresters (Item 1.1.1.7 - Supply of 110 kV Surge arresters (1-p) on neutral point of Transformer T5 – T6 including necessary steel structure, cabling and earthing - 2 pcs). Поясните, а для Т3 - Т4 еще 2 шт. не предусмотрены?; - 110 kV Current transformer (Item 1.1.1.9 - Supply of 110 kV Current transformer (1-p) including necessary steel structure, cabling and earthing - 9 pcs) - as per SLD 18 pcs. Where is mistake and which version is correct? | I ask you to read carefully the Particular specification for Vanadzor-1 substation: is have been implemented particular reconstruction It is included in VT bay unit.
|  | - Specifications of 6 kV Surge arresters for indoor applications are Missed- 6 pcs. | 6 kV Surge arresters should be included in VT bay.
3 | As per SLD(Appendix 17 -220kV Ashnak substation single line diagram Ц to realize): | - 220 kV Circuit breackers (Item 1.1.1.1 Supply of 220 kV Circuit breackers (3-p) including necessary steel structure, cabling and earthing - 1 pcs) - there is no way to assess the feasibility of, and in what part of the circuit is set 3-pole circuit breaker 220 kV, in addition, do you really need only one such CB? - 220 kV Circuit breackers (Item 1.1.1.2 Supply and of 220 kV Circuit breackers (1-p) including necessary steel structure, cabling and earthing - 9 pcs) - excluding one three-pole switch (if it is so), there are still 7 pcs. three-phase circuit breackers by 1 pole - 1 drive. Total = 21 pcs., But not 9 pcs. Where is mistake and which version is correct? - 220 kV Current transformer (Item 1.1.1.8 - Supply of 220 kV Current transformer (1-p) including necessary steel structure, cabling and earthing - 12 pcs) - on drawings there are 8 complects as 3-phaze - 24 pcs. Where is mistake and which version is correct? | I ask you to take carefully attention the Particular specification for Ashnak substation : is have been implemented particular reconstruction. Regarding the circuit Breackers - they should be 4 pcs: one (AT-2) should be threpole operated, other three CBs- onepole operated.
4 |  | In technical specifications of equipment (ICB_4 Substations_HVEN_04.09.15.pdf) there are not presented the characteristics of follow devices : - For the power transformers in Vanadzor-1 substation - data of power transformers are missed - Rehabilitation of existing Transformer 40МVА 110/10/10 kV including necessary steel structure, cabling and earthing - 2 pcs. - data are missed ; - Rehabilitation of existing Transformer 40МVА 110/6/6 kV including necessary steel structure, cabling and earthing - 2 pcs. - data are missed; 2.1. Also there are absent the data sheets for power equipment, involved in all specifications for SS, also there are absent the single line diagrams of connections for that devices - - Supply of Transformer automatic sprinkler system including transformer monitoring system, water pumps, necessary steel structure, cabling and earthing It is neccessary to clarify because it is not clear what to propose. | Attached enclosed the rate name plates of transformers to rehabilitated.
5 |  | In technical specifications of equipment (ICB_4 Substations_HVEN_04.09.15.pdf) the total complect of protection devices on HV and ML side is not mentioned . - the requirements for protection system equipment, the data sheets and preferable characteristics are absent, ; - in general specification are mentioned quantity of line protections and differencial busbar protection 220-110 kV, but the requirements regarding the protection of power transformers are missed in all cases; - Requirements regarding the busbar , fiders protection in 6, 10 kV switchgears are not mentioned. Or the protection system schemes sould be developed by bidder? In that case it is required to have requirement specifications. | I suggest you to look through pages N 809-913
|  | - Is it required the protection on Arapnja-1 and Arapnja-2 lines in drwing of Vanadzor-1 SS? | no