## 4 Substations Rehab
Questionnarie N 2 regarding the project of reconstruction of Haghtanak, Charentsavan-3, Vanadzor-1 and Ashnak substations
# | Specification | Chapter | page | Topic | Question | Reply
1 | 4.19. General Technical Specifications – HVEN- HAGHTANAK - General requirements for the protections of 220kV Substation connections |  | 891 | disturbance recorder device | Please clarify if it is allowed to offer the disturbance recorder functionality as integral part of the protection relays and without an independent disturbance recorder device. | No, they should be different devices
2 | 1. Scope of Supply of Plant and Installation Services by the Contractor | 1.1.6.4.3. | 146 | RTU | According to the tender one new RTU must be supplied. We have two questions: 1.Is it possible to quote one bay control unit per feeder, which directly acquires the HV feeder signals and sends them to the Gateway in the DCS. 2. Is it possible to combine one protection relay and one HV bay control units in the same device for bus coupler, line or transformer feeder (similar to MV)? For both solutions a RTU is not necessary. Please confirm this. | Regarding item 1. Yes, each feeder should have it`s separate bay control unit. 2. No, protection relay and bay control units should be in different devices, as per Bidding documents . Yes , RTU is not necessary.
3 | Section IV Bidding forms |  |  | Existing and new RTU for Haghtanak and Ashnak | According to the tender the existing RTU has to be reconnected to the new HV equipment and in addition a new RTU / Gateway has to be provided. We have two questions: Can the gateway / RTU of the new DCS be used as the new RTU described in 1.2.4.6.3? The new RTU will be supplied and therefore we kindly ask to remove the existing RTU and replace it through the requested new one, as the costs for the customer are lower in this case. | Answer will be sent after discussing with System Operator
4 | 1. Scope of Supply of Plant and Installation Services by the Contractor | 1.1.6.4.2 | 309 | Station Unit and Gateway | Please confirm if one multiprocessor based station unit, which owns separated CPUs and communication modules for the respective function (communication to IEDs, gateway to SCADA) can be offered as Station Unit and Gateway at the same time. | No
5 | 1. Scope of Supply of Plant and Installation Services by the Contractor | 1.1.6.4.3. | 310 | existing SCADA | Please clarify which is the mentioned existing SCADA (RCC, load dispatch center)? How many SCADA connections are requested from each gateway? | Answer will be sent after discussing with System Operator
6 | 4.18. General Technical Specifications – Requirements for the metering complex systems |  | 561 | Integration of metering system | Please confirm that the inquired metering system must not be interfaced to the DCS | The metering system devices have their own network, it is not required to be interfaced to the DCS.
7 | 4.19. General Technical Specifications – HVEN- HAGHTANAK - General requirements for the protections of 220kV Substation connections |  | 889 | 110kV busbar protection 220kV busbar protection | Please confirm if one modular centralized busbar protection relay is acceptable for the protection of the busbar and bypass of the respective substation voltage level (220kV and 110kV). | No, as it is required in Bidding documets.
8 | 4.2. General Technical Specifications - Digital Control System (DCS) | 5. | 635 | THE IEC 61850 ETHERNET NETWORK | Our IEDs own internal switches supporting RSTP / PPR / HSR, so that the IEDs are connected between them using fiber optical cables for a better electromagnetic compatibility. In addition in case of maintenance of primary equipment or cable connections / wiring it is possible to switch off control and monitoring of the electrical circuits by means of dedicated MCB, while IED is switch on and communicating. The bay can be switched to test mode by means of key-switch or function-key. Please confirm if our concept is acceptable. | Yes, fiber optical cables can be used . In that case they should be protected from rodents.
9 | Section IV Bidding forms |  | 77 | Remote end at Shahumyan 2 substation | Please clarify if the requested new control and protection equipment for the Remote end at Shahumyan 2 substation, must be integrated in the existing DCS of the Shahumyan 2 substation. | Yes
10 | 4.19. General Technical Specifications – HVEN- HAGHTANAK - General requirements for the protections of 220kV Substation connections |  | 889 | AT protections - Protection for the general part of winding | Please confirm if the overload protection of winding can be integrated in one of the requested devices (differential protection or 220kV distance protection or 110kV distance protection or Bay Control Unit). | Yes
11 | 4.19. General Technical Specifications – HVEN- HAGHTANAK - General requirements for the protections of 220kV Substation connections |  | 890 | Protection for boost transformer and 10kV incoming transformer | Please confirm if the requested transformer Back-up microprocessor device on 10kV also protects the 10kV boost transformer and controls, protects and monitors the respective 10 kV incoming feeder circuit breaker. | No, it should be separate devices
12 | 4.19. General Technical Specifications – HVEN- HAGHTANAK - General requirements for the protections of 220kV Substation connections |  | 890 | Protection's function of 6kV or 10kV lines | Please confirm if the requested 6kV or 10kV busbar differential protection (logic) scheme can be implemented according to the reverse interlocking principle. | Yes