## Tabelle1
No.: | Date | Refernce (Lot, Document, chapter,page) | Issue | Question Bidder | Answer Employer
Clarif. No. 1 sent 20/10/2015 (click on cross to open)
1 | 2015-10-20 | "ICB_4 Substations_HVEN_04.09.15.pdf" Page 295/1036 Chapter 1.1.2.7.1 (General) | Training | “Training for overhead lines” We will not be responsible for OHLs. We assume not to do related training.
2 | 2015-10-20 | "ICB_4 Substations_HVEN_04.09.15.pdf" Page 349/1036 (Vanadzo-1) | Trafo repair | Requirement: two (2) Transformers 110/10 kV 40 MVA to rehabilitate; two (2) Transformers 110/6 kV 40 MVA to rehabilitate; For evaluation of current transformer conditions we need the following: - Manufacturer - Manufacturer- / commissioning date - technical data (rating plate) - PD-measurement / analyze - oil in gas analysis - failure suffered by the transformer
3 | 2015-10-20 | "ICB_4 Substations_HVEN_04.09.15.pdf" Page 377/1036 (Ashnak) | Trafo repair | Requirement: one (1) Autotransformer 220/110/10 kV 63 MVA to repair; two (2) Boost transformers 10/10 kV 40 MVA to repair; Repairing and painting with anti-corrosion paint of existing House transformers 10/0.4 kV 630 kVA; For evaluation of current transformer conditions we need the following: - Manufacturer - Manufacturer- / commissioning date - technical data (rating plate) - PD-measurement / analyze - oil in gas analysis - failure suffered by the transformer
4 | 2015-10-20 | General question / all lots | Drawings | In order to do proper determination of scope and to find the best technical solution we need following as build drawings from existing substations: 1. Building 2. Drainage / sewerage system 3. Cable routes 4. Layouts, sections 5. Foundation plan We need from the layouts / sections the workable files *.dwg for example or other format in order to implement new equipment.
5 | 2015-10-20 | General question / all lots | Workable docs | We need for tender preparation we need following documents in workable files: 1. Price lists as *.xls
6 | 2015-10-20 | General question / all lots | Tender docs in Armenian | Please send us the tender documentation in Armenian.
7 | 2015-10-20 | "ICB_4 Substations_HVEN_04.09.15.pdf" Page 476/1036 Data sheet 110 kV disconnector | Operating device 110 kV disconnector | Operating device for 110 kV disconnector "single pole" requested. Could we offer instead of "single pole" "three pole" devices - means one drive for all three poles? In substations Vanadzor-1 and Allaverdi-2 three pole devices are installed. Devices will be cheaper and cabling also.
8 | 2015-10-20 | General question / all lots | Soil investigation | For the existing substations we need the soil investigation reports.
Clarif. No. 2 sent 23/10/2015 (click on cross to open)
9 | 2015-10-23 | "ICB_4 Substations_HVEN_04.09.15.pdf" Page 33 and 37/1036 ITB 11.1(k), ITB 21.1 | documentation-format | In ITB 11.1 (k) is requested submission of price list in MS-Word format and in ITB 21.1 MS-Excell. Please confirm MS-Excell as format for price lists.
10 | 2015-10-23 | "ICB_4 Substations_HVEN_04.09.15.pdf" Page 37 and 37/1036 ITB 21.1 | Doffer documentation | Requested offer documentation comprises of one original and three copies. As the postqualification documents nearly the same for each lot - please confirm that documents valid for all lots can be submitted in one original and three copies for all lots together (one time only) and not for each lot separately.
11 | 2015-10-23 | "ICB_4 Substations_HVEN_04.09.15.pdf" Page 316/1036 and "Appendix 8 -220kV Haghtanak substation Ц Environmental Management Plan.pdf" page 4/19 | refurbishment / new construction of control building | In mentioned documents are contradiction concerning new construction or refurbishment of control building. Please confirm that refurbishment is requested.
12 | 2015-10-23 | General question / all lots "ICB_4 Substations_HVEN_04.09.15.pdf" | Workable docs | We need for tender preparation we need following documents in workable files: 1. Tender as *.doc (not available on submitted CD) for filling the requested information in Forms and Technical Schedules.
13 | 2015-10-23 | "ICB_4 Substations_HVEN_04.09.15.pdf" Page 316/1036 and "Appendix 8 -220kV Haghtanak substation Ц Environmental Management Plan.pdf" page 4/19 | Ambient temperature | In mentioned documents are contradiction concerning ambient temperature: -35°C - + 50°C and -28°C-42°C (Environmental Management Plan). Please confirm temperature range -28°C up to 42°C as indicated in the Environmental Management plan.
14 | 2015-10-23 | "ICB_4 Substations_HVEN_04.09.15.pdf" Pagees 556-569/1036 | Technical Schedules | Technical Schedules for Auto-transformers contains unreadable characters: a) Page 556 item 8 b) Page 558 item 6 c) Page 567 item 8 d) Page 569 item 6 Please send us current file with readable characters.
15 | 2015-10-23 | "ICB_4 Substations_HVEN_04.09.15.pdf" Pagees 556-569/1036 | Trafo losses | Please confirm that guaranteed and capatilized values of the short-circuit losses for all transformers is based on ONAN mode.
Clarif. No. 3 sent 27/10/2015
16 | 2015-10-27 |  |  | Please instruct us or show exact location, where we must transport or dispose all dismantled equipment, so we can calculate properly highlighted point. | In Haghtanak SS all dismantled equipment should be removed to Shahumyan-2 SS - aprox 3 km. In Ashnak and Charentsavan-3 substations dismantled equipment should be stored at the same substations in previosly prepared temporary open storages. In Vanadzor-1 SS dismantled equipment should be stored at substation area.
17 | 2015-10-27 |  |  | What exactly means Auto transformer sprinkler automatic system? | It is an automatic fire fighting sprinkler sysytem for autotransformers.
18 | 2015-10-27 | ITB 7.1 of BDS |  | The equipment required in Section III. Evaluation and Qualification Criteria contains “Truck with aerial lift” and “Compress matrix”. According to ITB 7.1 of BDS we would like to clarify the following: Truck with aerial lift is the self-loader with hydraulic or pneumatic arm, or it is the car with lifting basket for workers on it. What is the necessary capacity of Compress matrix. | Truck with self - regulating hydraulic arm. The capacity of Compress matrix should be considered by works specifications which should be implemented in substations.
19 | 2015-10-27 | "ICB_4 Substations_HVEN_04.09.15.pdf" page 385, point 1.1.2.19 |  | In the heating and air conditioning system in the technical specification it is required study, supply, installation and connection of equipment of heating and air conditioning in every room of control building, 10kV building and guard room, but the title of Armenian version of the same document requires Air conditioning with hydration (page 385, point 1.1.2.19). Please clarify. | English version should be considered.
20 | 2015-10-27 | "ICB_4 Substations_HVEN_04.09.15.pdf" page 315, point 1.1.6.14.2 (Armenian version page 387, point 1.1.2.23 |  | We need detail explanation for one of the points in tender technical specification Civil works (English version, page 315, point 1.1.6.14.2) The replacement of the existing equipment support frames made in concrete and the construction or rehabilitation of their foundations. (Armenian version page 387, point 1.1.2.23) It says replacement of existing steel structures from inside of existing concrete foundations, in our opinion it is impossible to extract any steel structure from existing concrete foundation without braking or destroying them, so afterwards there will be a need to make new foundations, but not their rehabilitation. Please clarify. | English version should be considered.
21 | 2015-10-27 | "ICB_4 Substations_HVEN_04.09.15.pdf" point 1.1.17.17.2 |  | In the point 1.1.17.17.2. of Ashnak SS there is a task about foundations and we understand that new foundations will be made only for new equipment and for all other equipment together there should be rehabilitated only 4 foundations? Please clarify. | Foundations of 4 bays should be rehabilitated and foundations of those constructions, which will be used during substations future maintenance.
22 | 2015-10-27 | Ashnak |  | In Ashnak SS, shall we construct new control building or rehabilitate the existing one, or if we make a new control building, what shall we do with the old one? Dismantle and disposal or leave like it is. | It is a subject of dismanlting.
Clarif. No. 1 sent 20/10/2015 (no clarification)
Clarif. No. 2 sent 23/10/2015 (no clarification)
Clarif. No. 3 sent 27/10/2015
100 | 2015-10-27 |  |  | Automatic Voltage Regulation relays for AT/T are not mentioned in tender documentation. Is it necessary to provide it? In case of "yes" please specify types of equipment to be equiped. Автоматика управления РПН не упомянута в тендерной документации. Её необходимо поставить? Если "да", то определите, пожалуйста, для каких (авто)трансформаторов её предлагать. | Requirements mentioned on page 913.
101 | 2015-10-27 |  |  | BCU for 10kV is mentioned only in DCS redundant architecture. In RfQ is mentioned only switch. Is it necessary to provide BCU and switches for 10kV? Контроллер(ы) BCU для РУ 10 кВ упомянуты только на архитектуре SCADA и их нет в "Объёме поставки", в требованиях текстом прописаны только коммутаторы для реле. Что необходимо предложить для РУ 10 кВ? | Yes .
102 | 2015-10-27 |  |  | No scope of supply of protection for remote ends are mentioned in RfQ except two 110kV OHLS in Haghtanak S/S. Защиты обратных концов ВЛ указаны только для 2-х ВЛ 110 кВ с ПС Хагтанак и не указанаы для всех остальных ВЛ. Это верно? | Yes, as it is mentioned in technical specifications .
103 | 2015-10-27 |  |  | If any digital protection relay is already installed in substations, it will be exchanged completely including cubicle as requested in Material requisition schedules. Если на какой-то из ПС уже были установлены цифровые реле, то они подлежат замене в соответствии с "Объёмом поставки"? | Yes .
104 | 2015-10-27 |  |  | Is it allowed to supply protection panel with other dimensions as requested, e.g. in Gymri-2: H2000+200mm * W900mm * D600mm Можно ли предлагать шкафы иного размера, нежели запрошенный, например, такие, как для проекта Гюмри-2 (2000+200х900х600)? | No, as it is mentioned in technical specifications .
105 | 2015-10-27 |  |  | In RfQ is requested to supply new PLC at local and remote end. In Material requisition schedule is requested only reinstallation. What is requested? In cse of re-installation of existing PLC please provide all technical documentation for panels. В ТЗ указана установка новых PLC на реконструируемых ПС и обратных концах ВЛ, при этом в "Объёме поставки" указана только переустановка существующих PLC. Что в итоге нужно сделать? Если переустановить имеющиеся PLC, то просим предоставить техническую документацию по ним. | Technical documentation should be provided later.
106 | 2015-10-27 |  |  | In RfQ is requested to exchange meters with cubicle only. Exchange of software, PC, HMI of metering is not requested. In Material requisition schedule is nothing requested. What is requested? В ТЗ указана замена счётчиков АСКУЭ в комплекте со шкафами. Замена ПО, компьютеров не требуется. В "Объёме поставки" счётчики не упоминаются. Что нужно сделать? | It is requested to replace meters and foreseen cubicles.
107 | 2015-10-27 |  |  | Emergency control automatic is requested only in RfQ. In Material requisition schedule is nothing mentioned. Is it necessary to provide it and in case of “yes” is it allowed to activate requested ECA functions in new protection terminals. Противоаварийная автоматика упоминается в ТЗ. В «Объёме поставки» нет такого оборудования. Нужно ли его поставлять и елси да, то допускается ли активировать соответствующие функции в терминалах РЗА? | It is necessary to activate in RP devices.
108 | 2015-10-27 |  |  | Testing equipment (Omicron) is requested in Material requisition schedule for Haghtanak only. Is it requested in Ashnak too? Тестовое оборудование (типа Omicron) в соответствии с "Объёмом поставки" запрошено только для ПС Хагтанак. Нужно ли поставлять аналогичное оборудование для ПС Ашнак? | As it is mentioned in tecnical specifications .
109 | 2015-10-27 |  |  | Telecommunication equipment is requested in RfQ. What should be done if there is any existing modern telecommunication equipment? Телекоммуникационное оборудование упомянуто в ТЗ. Что нужно делать с установленным на ПС телекоммуникационным оборудованием, если таковое имеется? | It should be provided later.
110 | 2015-10-27 | "ICB_4 Substations_HVEN_04.09.15.pdf" Pages 308-309 |  | Energy meters (308) What brand of energy meter shall be used? Is a redundant Solution required (main & control meter) DCS (page 309) IED…multifunctional relays in MV: does it mean protection relays with control facilities? ՀԱշվիչներ . Ինչ ֆիրմայի հաշվիչներ պետք էօգտագործվի՞ Պահանջվում է հավելյալ հիմունքներով լուծում (հիմնական և հսկող հաշվիչ) : ԹՂՀ . IED .. բազմաֆունկցիոնալ ռելեներ ՄԼ համար. Դա նշանակում է պաշտպանության ռելեներ ղեկավարման ֆունկցիաներով՞: | Existing meters should be used, only cubicles should be changed.
111 | 2015-10-27 | "ICB_4 Substations_HVEN_04.09.15.pdf" Pages 310 |  | Telecontrol (page 310) If signals, commands and measurements are transferred via gateways, no RTUs are needed, can you confirm? Do you require FO patchpanels as well? Հեռակառավարում (էջ 310) Եթե ազդանշանները, հրամանները և չափումները տեղափոխվում է ուղեկապերով, RTU- ների անհրաժեշտությունը չկա, կարող էք հաստատել՞: Դուք պահանջում էք նաև FO կոմուտացիոն վահաններ՞ | It should be provided later.
Clarif. No. 1 sent 20/10/2015 (no clarification)
Clarif. No. 2 sent 23/10/2015 (no clarification)
201 | 2015-10-27 |  |  | Absolute minimum temperature in the tender documentation is -35°C for all substations and different temperature for each Substation in the environmental management plan (Haghtanak: -28°C, Ashnak: ?, etc.) | Data mentioned in Particular specifications should be considered.
201 | 2015-10-27 |  |  | В тендерной документации для всех подстанций указана минимальная температура воздуха -35°C, в приложении к тендеру "environmental management plan" указаны другие температуры для каждой ПС (Haghtanak: -28°C, Ashnak: ?, etc.). что считать правильним?
202 | 2015-10-27 |  |  | Please inform about nominal currents for each bay for each Substation (for each voltage level) | Required data are mentioned in technical data
202 | 2015-10-27 |  |  | Пожалуйста предоставьте номинальние токи всех ячеек на каждой подстанции для каждого уровня напряжения
203 | 2015-10-27 |  |  | Please inform about short-circuit current for each substation for earthing and primer-design | See attached shedule on the Tabelle 2 of this fail
203 | 2015-10-27 |  |  | Пожалуйста предоставьте рарасчетные токи короткого замыкания на каждой подстанции для разработки заземления и первичного проектирования
204 | 2015-10-27 |  |  | Please provide following items for each substation:
204.1 | 2015-10-27 |  |  | Пожалуйста предоставьте следующие документы для каждой подстанции:
204.2 | 2015-10-27 |  |  | -low voltage cable plan /план расположения низковольтных кабелей | data mentioned in existing layouts should be considered.
204.3 | 2015-10-27 |  |  | -earthing plan / план заземления | Should be implemented by Contractor .
204.4 | 2015-10-27 |  |  | -foundation plan / план расположения фундаментов
204.5 | 2015-10-27 |  |  | -lighting protection / грозозащита
204.6 | 2015-10-27 |  |  | -sections of bays / разрезы ячеек
204.7 | 2015-10-27 |  |  | -layouts and sections of existing buildings (MV switchgear building, control building etc.) / чертежи и разрезы зданий (здание распредустроиства среднего напряжения, здание РЗА и т.д.) | Are mentioned in plans of substations provided previously .
204.8 | 2015-10-27 |  |  | -PLC architecture and frequencies / архитектура ВЧ-связи и частоты | It should be provided later.
204.9 | 2015-10-27 |  |  | -existing transformer (AT, T, boost transformer, auxillary) mechanical drawings and foundation drawings / чертежи существующих трансформаторов и их фундаментов (АТ, Т, линейные тр., тр. собственних нужд) | Transformers data on name plates have been provided previously .
205 | 2015-10-27 |  |  | Please confirm that all 110kV disconnectors for each substation must be supplied with one operating motor for three phases (three phase operated) | Yes
205 | 2015-10-27 |  |  | Пожалуйста подтвердите, что разъединители 110кВ, для каждой подстанции, должны поставляться с одним управляющим приводом на три фазы
206 | 2015-10-27 |  |  | Please confirm that all 220kV disconnectors for each substation must be supplied with one operating motor for each phase (single phase operated) | Yes
206 | 2015-10-27 |  |  | Пожалуйста подтвердите, что разъединители 220кВ, для каждой подстанции, должны поставляться с одним управляющим приводом на каждую фазу
207 | 2015-10-27 |  |  | Is it allowed to install the 10kV bays in SS Ashnak in one row?
207 | 2015-10-27 |  |  | Допускается ли установка ячеек 10кВ в один ряд? | If possibility of buildings and temporary scheme will allow.
208 | 2015-10-27 |  |  | In Ashnak S/S is requested: 2pcs. 220kV CB - one pole operated, 2pcs. 220kV CB - three pole operated. Please confirm. | It should be 4 pcs of three phase 220 kV Circuit Breakers, one of them with 3 pole operation and three with 1-pole operation.
208 | 2015-10-27 |  |  | В объем поставок ПС Ашнак входит: два силовых выключателя 220кВ с приводом на каждую фазу и два силовых выключателя 220кВ с одним приводом на три фазы. Пожауйста подтвердите.
209 | 2015-10-27 |  |  | Same CBs could be supplyed? Можно ли поставлять одинаковые выключатели? | No
Clarif. No. 1 sent 20/10/2015 (click on cross to open)
200 |  | ITB, clause 2.3 and Section IX, Contract Forms, Appendix 1 | Payment | According to ITB, clause 2.3 and Section IX, Contract Forms, Appendix 1, Payment Procedures and Contract Agreement Form, Clause 2.2 payments shall be effected as follows: (i) For advance payment and for Plant and Equipment supplied from within the Employer’s Country. Design Services and Installation Services shall be made by direct disbursement from the World Bank, and (ii) For Plant and Mandatory Spare Parts supplied from Abroad shall be made our through a confirmed irrevocable divisible documentary Letter of Credit to be opened by the Employer under the World bank Special Commitment Procedure in favour of the Contractor. All charges for the opening of the confirmed Letter of Credit are to be borne by the Employer. Please confirm if our understanding is correct or advice.
201 |  | Section IX, Contract Forms, Appendix 1 | Bonds | According to Section IX, Contract Forms, Appendix 1, Payment Procedures last paragraph is stated that “ The Contractor shall instruct its bank to issue and advance payment security made available to the Contractor in a bank in the country of the Employer”. The wording is not understandable. Advance Payment Securities or Performance Bonds provided by a foreign Contractor shall be issued by a First Class Bank of Contractor’s home country and advance Payment Securities or performance Bonds provide by a local Contractor to be issued by a bank in the country of the Employer. Please confirm.
202 |  | ITB, Bid Data Sheet, Particular conditions | Price adjustment | We have noted, that according to the ITB/Bid Data Sheet and Bidding Forms, Price Adjustment, the prices of the price schedule 1, price schedule 2 and price schedule 4 shall be subject to adjustment during the performance of the contract as per the Price Adjustment Formula. Please confirm if our understanding is correct or advice.
Clarif. No. 2 sent 23/10/2015 (no clarification)
Clarif. No. 3 sent 27/10/2015
203 |  |  |  | According to bidding documents Section 1 instructions to bidders, point 18. Currencies of Bid and Payment, we as a resident partner of the consortium, for our part of done works, shall price and later invoice our payment certificate only in Armenian drams (AMD), since between 2 resident companies cannot be used other currency than national currency (Dram) according to the law. Please give your no objection concerning abovementioned issue | We have no objection in regards of above mentioned issue.
204
205
206
207

## Tabelle2
NN | Substation | Short - circuit currents
|  | I (3)max (kA) |  |  |  | 3I 0 (1.1) max (kA)
|  | 220 kV | 110 kV | 10 kV | 6 kV | 220 kv | 110 kV
1 | Ashnak | 9.4 | 7.2 | 14.3 |  | 9 | 7.7
2 | Aghtanak | 16 | 19.7 | 33 |  | 15.5 | 20.7
3 | Vanadzor-1 T-3, T-4, T-5, T-6 |  | 12.3 | 18.5 | 17 |  | 13.2
4 | Charentsavan-3 |  | 13.1 | 12.3 |  |  | 12.9