## Лист1
[5 empty] | Quastion | Replay
3 | Section IV Bidding forms |  |  | Existing and new RTU for Haghtanak and Ashnak | According to the tender the existing RTU has to be reconnected to the new HV equipment and in addition a new RTU / Gateway has to be provided. We have two questions: Can the gateway / RTU of the new DCS be used as the new RTU described in 1.2.4.6.3? The new RTU will be supplied and therefore we kindly ask to remove the existing RTU and replace it through the requested new one, as the costs for the customer are lower in this case. | The Existing RTU should remain with its all physical connections . Besides it in the DCS should be foreseen the Gateway device which will be able to transfer all necessary volume of information to System Despatch Center by IEC 870-5-104 protocol
5 | 1. Scope of Supply of Plant and Installation Services by the Contractor | 1.1.6.4.3. | 310 | existing SCADA | Please clarify which is the mentioned existing SCADA (RCC, load dispatch center)? How many SCADA connections are requested from each gateway? | The Existing control system is SCADA system of System Dispatch Center , which is equivalent to RCC. The number of connection Getaways should be at least 4, 2 of which should answer to two Front/End parallel servers of SCADA system and other 2 should be foreseen for the connection with SCADA system of future backup dispatching Center.