## Sheet1
Contract No. and Title: HV-W-ESRAF-1/2015
SUBJECT: Rehabilitation of 220 kV “Haghtanak”, 110 kV “Charentsavan-3”, 110 kV “Vanadzor-1” and 220 kV “Ashnak” Substations
|  | Subject | Query | Answer
COMMON
1 | Section-VI, Employer Requirement Genetral, Clause 1.1.2.2.4 | Engineering Design and Drawings submission | We understand that all design & drawing submission during project execution shall be in English language. Russian / Armenian language is not mandatory for design/drawings submission. Please confirm. | As per PC (page 997) Armenian translation is mandatory.
2 | Section-VI, Employer Requirement Genetral, Clause 1.1.2.2.5 | Engineering Design and Drawings approvals | We understand that Employer only review all the design / drawings for approvals. Any outside consultant / University committee will not be involved in approval process. Please confirm. | Please consider item 1.1.2.2.1 on page 280.
HAGHTANAK
3 | Section-VI, Employer Requirement Scope of works - Clause 1.1.3.3.2 | 220kV Substation | We understand that existing 220kV substation is in live condition and all equipment/conductors/ hardware/insulators etc are to be replaced with new equipment / accessories. As substation is in live condition, we presume that existing busbar gantries and bay gantry structures are to be used for proposed rehabilitation work as dismantling of busbar gantries and bay gantries is not possible in live substation and requires long shutdowns. Pleas confirm that our understanding is correct. | Gantries should be subject of repair, not replacement. Regarding the outages they will be carried out in stages, on which the contractor will submit it's proposals.
4 | Section-VI, Employer Requirement Scope of works - Clause 1.1.6.1.5 | 220kV Busbars | Please confirm 220kV Busbar rating. Also please furnish conductor type/size and configuration such as Single/Twin/Quad. We understand that as existing conductor is in live condition, existing busbar gantries to be used for proposed rehabilitated substation. Only new conductors/hardware/insulator strings are to be supplied and installed as per requirement. Please confirm. | Yes, your consideration is correct. Only equipment should be replaced. Type of Existing conductor in SS is AC 500. Busbar should be supplied and installed.
5 | Section-VI, Employer Requirement Scope of works - Clause 1.1.6.1.9 | 110kV Busbars | Please confirm 110kV Busbar rarting. Also please furnish conductor type/size and configuration such as Single/Twin/Quad. | Capacity of 110 kV busbar is 800A.
6 | Section-VI, Employer Requirement Scope of works - Clause 1.1.3.3.7 - Clause 1.1.3.3.8 | Control Building 10kV Switchgear Building | We understahnd that existing control building & 10kV switchgear builiding has sufficient place to install new 220kV & 110kV control protection panels and 10kV switchgears without dismantling existing panels / switchgears. As existing 220kV substation is in live state dismantling of any existing panels is not possible. | In generally condition yes, but it is possible to carry out the dismantling works as per outages stages.
7 | Section-VI, Employer Requirement Scope of works - Clause 1.1.6.3.1 - Clause 1.1.6.4.1, 1.1.6.4.2, 1.1.6.4.3 - Clause 1.1.6.5.1, 1.1.6.5.2, 1.1.6.5.3 | Protection, Control & Telecommunication | We understand that complete new protection panels are to be supplied for 220kV, 110kV & 10kV bays under scope of works. Also new substation automation system (SCADA) shall be provided for complete substation along with new Telecommunication system. Please confirm. Also confirm that the after the completion of rehabilitation of substation old control system shall be dismantled and will not be in use. | Yes.
8 | Section-VI, Employer Requirement Scope of works - Clause 1.1.6.13.1 | Earthing system | Please confirm scope for earthing system. Complete new earthing system is to be provided including existing 220kV system? | Yes.
9 | Section-VI, Employer Requirement Scope of works - Clause 1.1.6.3.1 (Protection) | Protection panels for remote end substations | We presume that any work related to protection system is not involved in 220kV remote end substations i.e Hakhtanak and Erebuni. Please confirm. | Yes.
10 | Section-VI, Employer Requirement Scope of works - Price schedule sr. 1.1.3.1 - Technical data sheet | 110kV Circuit Breaker | We understand that all 110kV CBs including for Line bays shall be three pole operated with common operating mechanism for three poles. Please confirm. | Yes.
11 | Section-VI, Employer Requirement Scope of works - Technical data sheet | 220kV Circuit Breaker | We understand that all 20kV CBs including for Line bays shall be single pole operated with separate operating mechanism for each pole. Please confirm. | It is correct for Haghtanak SS.
12 | Section-VI, Employer Requirement Scope of works - Technical data sheet | Auto Transformer -220/110/10kV, 63 MVA 220/110/10kV, 125 MVA | In technical data sheet, rated voltages are mentioned as 252kV, 126kV & 12kV. The same shall be 245kV, 123kV & 11kV. Please review and confirm. | 245kV, 123kV & 12kV should be considered.
13 | Section-VI, Employer RequirementScope of works-Single line diagram | Limit of scope | We understand limit of scope as under -- For 220kV Line take off gantries, Line side insulator strings are not in scope of works. Only jumper connection from TL to substation equipment shall be in scope.- For 110kV Line take off gantries, Line side insulator strings are not in scope of works. Only jumper connection from TL to substation equipment shall be in scope.- For 10kV portion, only incomer cables upto 10kV switchgear shall be in scope. Any cables/termination kits for outgoing feeders are not in scope of works.Please confirm whether above understanding is correct. | Generally scope includs line gantries. For 6, 10kV portions as per Bidding documents outgoing cables upto sustation's border should be in scope.
14 | Section-VI, Employer Requirement Scope of works - Price schedule 1.1.2.6 (Sch- 1) - Price schedule 1.2.10 (Sch- 4) | Transformer fire fighting water supply | For transformer water spray fire fighting system, water tank will be required for the storage of water. Please clarify the following for scope of water tank for the same - 1. Whether water tank is overhead or underground 2. Capacity of the water storage tank 3. Location of the water tank as this will affect the piping works and pump capacities. | New underground water pool should be designed and constucted, which capacity shall be calculated taking into consideration oil volume of transformers located in subsation.
15 | Section-VI, Employer Requirement Scope of works - Price schedule 1.3.2 | Fire detection | Please confirm scope of works for fire detection system. Please clarify whether the same is to be provided for complete existing control building and 10kV switchgear building. | Yes.
CHARENTSAVAN
1 | Section-VI, Employer Requirement Scope of works - Clause 1.1.8.3.3 | 110kV Substation | We understand that existing 110kV substation is in live condition and all equipment/conductors/hardware/insulators etc are to be replaced with nee equipment / accessories. As substation is in live condition, we presume that existing busbar gantries and bay gantry structures are to be used for proposed rehabilitation work as dismantling of busbar gantries and bay gantries is not possible in live substation and requires long shutdowns. Pleas we confirm that our understanding is correct. | Gantries should be subject of repair, not replacement. Regarding the outages they will be carried out in stages, on which the contractor will submit it's proposals.
2 | Section-VI, Employer Requirement Scope of works - Clause 1.1.11.1.8 | 110kV Busbars | Please confirm 110kV Busbar rating. Also please furnish conductor type/size and configuration such as Single/Twin/Quad. We understand that as existing conductor is in live condition, existing busbar gantries to be used for proposed rehabilitated substation. Only new onductors/hardware/insulator strings are to be supplied and installed as per requirement. Please confirm. | Capacity of busbar is 800A. Busbars should be supplied and installed, using gantries which shall be repaired.
3 | Section-VI, Employer Requirement Scope of works - Clause 1.1.8.3.2 | Control Building | Layout provided with tender document does not give information about new control building. Please furnish following information for control building- 1. Control building room layout with minimum floor area required. 2. New control building location. This will affect the quantities like control & power cables from various equipment to control/protection panels. | The Control building in Charentsavan-3 will be built parallel to the existing control building to the OSY area with shift approximately on 20 m to substation entrance . The Control building in Ashnak SS expected to build with dismantling of about 30% of the old building and extended it to the substation entrance. Room areas are specified depending on the size and design of the proposed facilities and will be corrected during the design stage.
4 | Section-VI, Employer Requirement Scope of works - Clause 1.1.11.1.3 | 110kV Line bays Zangu1, Zangu2,Lusavan1 & Lusavan2 | For these line bays any CVT or SA is not provided at line end. Please clarify whether the requirement is correct. Also please clarify how metering and protections are to be considered without any VT / CVT. | They are not necessary.
5 | Section-VI, Employer Requirement Scope of works - Clause 1.1.11.1.4 | 110kV Line bays Zangu1, Qaxsi1 & 2, Taron and Solak | For these line bays any SA is not provided at Line end. Please clarify whether the requirement is correct. | Yes.
6 | Section-VI, Employer RequirementScope of works-Clause 1.1.11.3.1, 1.1.11.3.2-Clause 1.1.11.4.1, 1.1.11.4.2- Clause 1.1.11.5.1, 1.1.11.5.2, 1.1.11.5.3 | Protection, Control & Telecommunication | We understand that complete new protection panels are to be supplied for 110kV & 10kV bays under scope of works. Also new substation automation system (SCADA) shall be provided for complete substation along with new Telecommunication system for rehabilitated 110/10kV substation. Other existing systems are not to be integrated with new DSC system.Please confirm.Also confirm that the after the completion of rehabilitation of substation old control system for 110/10kV substation shall be dismantled and will not be in use. | Yes.
7 | Section-VI, Employer Requirement Scope of works - Clause 1.1.11.3.1 (Protection) | Protection panels for remote end substations | We presume that any work related to protection system is not involved in 110kV remote end substations. Please confirm. | Yes.
8 | Section-VI, Employer Requirement Scope of works - Single line diagram | Limit of scope | We understand limit of scope as under - - For 110kV Line take off gantries, Line side insulator strings are not in scope of works. Only jumper connection from TL to substation equipment shall be in scope. - For 10kV portion, only incomer cables upto 10kV switchgear shall be in scope. Any cables/termination kits for outgoing feeders are not in scope of works. Please confirm whether above understanding is correct. | Yes. For 6, 10kV portions as per Bidding documents outgoing cables upto sustation's border should be in scope.
9 | Section-VI, Employer Requirement Scope of works - Price schedule sr. 1.1.1.1 - Technical data sheet | 110kV Circuit Breaker | We understand that all 110kV CBs including for Line bays shall be three pole operated with common operating mechanism for three poles. Please confirm. | Yes.
10 | Section-VI, Employer Requirement Scope of works - Price schedule 1.1.2.4 (Sch-1) - Price schedule 1.2.10 (Sch- 4) | Transformer fire fighting water supply | For transformer water spray fire fighting system, water tank will be required for the storage of water. Please clarify the following for scope of water tank for the same - 1. Whether water tank is overhad or undergroung 2. Capacity of the water storage tank 3. Location of the water tank as this will affect the piping works and pump capacities. | New underground water pool should be designed and constucted, which capacity shall be calculated taking into consideration oil volume of transformers located in subsation.
11 | Section VI, employer's Requirements, Clasue No. 1.2.4.7.1.1. | The telecommunications system includes: • a network of fibres optic cables on HV-lines (OPGW) between substations | Generally laying of OPGW between substations on HV lines done by Transmission Line contractors or in separate projects. Please confirm that the same is included in this package or not. | No .
12 | Section-VI, Employer Requirement Scope of works - Price schedule 1.3.2 | Fire detection | Please confirm scope of works for fire detection system. Please clarify whether the same is to be provided for existing 10kV switchgear building as well. | Yes.
13 | Clause No. 30 of GCC and Particular Conditions | Limitation of Liability | As per global standard practices, Limitation of liability shall kept as maximum upto 100% of contract value however for this project as per bidding documents it is 150% of contract value. Hence, we request you to keep the Limitation of Liability as 100% of contract value as per global standards and amend the clause accordingly. | It si the bidding documents requirements and is not a subject of change.