High Voltage Electric Networks CJSC

Rehabilitation of 220 kV “Haghtanak”, 110 kV “Charentsavan-3”, 110 kV “Vanadzor-1” and 220 kV “Ashnak” Substations

| Item No. | Tender Document Ref. | Query | Applies to (S/S or Lot) | Answer |
| --- | --- | --- | --- | --- |
| 1 | Section VI, item 1.1.6.1.3: | The 220kV VT’s shall be capacitive-type voltage transformer (VT 1-p) designed to be equipped with line traps (line traps are already installed), and 2 secondary windings. - Please provide drawings and technical data (dimension, weight, installation details, etc) about the Line Trap. - How is the installation of the LT foreseen? on top of VT, hanging in the Girder, on top of PI’s? | Lots 1, 2, 4 | Line traps are hanging on gantries or towers. At the same time we would like to remind you that line traps are not involved in scope of works. |
| 2 | Section VI, General requirements for the protections of 220kV and 110kV Substation connections | Specification text: “Foresee TDM (transformer insulator monitoring and diagnostic system) system for Transformers.” Please clarify if this is applicable and if so provide technical requirements for such system. | All | Installation of new monitoring and diagnostic system including : - Phase current A,B,C outgoing socket pin, - Tangents of phase A,B,C (%), - Shifting of phase A,B,C (degree), - Phase imbalance, - Phase capacitance (picofarad), - Partial discharge - Earthing (impulse/s), - Neutral (impulse/s), - Bushings 110/220 kV phase A,B,C - Humidity of environment (%), - Temperature of environment Co - Temperature of upper part of cooling Co, - Temperature inside device Co. |
| 3 | Price Schedules | In the Price Schedules, for supply of Autotransformers it is mentioned “including monitoring system”. Please specify the kind of monitoring system. | Lots 1, 2, 4 | Installation of new monitoring and diagnostic system including : - Phase current A,B,C outgoing socket pin, - Tangents of phase A,B,C (%), - Shifting of phase A,B,C (degree), - Phase imbalance, - Phase capacitance (picofarad), - Partial discharge - Earthing (impulse/s), - Neutral (impulse/s), - Bushings 110/220 kV phase A,B,C - Humidity of environment (%), - Temperature of environment Co - Temperature of upper part of cooling Co, - Temperature inside device Co. |
| 4 |  | Boost transformer 40 MVA 10/10 kV - Please specify the number of bushings for HV side (in the specification it states 4 bushings: phase + neutral, connection group is Dd4) . | Lot 1 | Connection group of Boost transformer is Y-Y-0. |
| 5 |  | Autotransformer 125 MVA 220/110/10 kV - Please specify the Insulation levels for the HV-N (LI/AC=? kV) - | Lot 1 | Insulation level for 220 kV side consider as 400 kV. |
| 6 |  | Autotransformer 63 MVA 220/110/10 kV Please specify the Insulation levels for the HV-N (LI/AC=? kV) - | Lot 4 | Insulation level for 220 kV side consider as 400 kV. |
| 7 |  | Transformer 25 MVA 110/10 kV - Please specify the Insulation levels for the HV-N (LI/AC=? kV) - | Lot 2 | Insulation level for 110 kV side consider as 200 kV. |
| 8 | Section VI, 1.1.6.1.13: | Are Marshalling Kiosks dedicated to the local control of each 220kV and 110kV Feeder required? | Lot 1 | As per mentioned item 1.1.6.1.13: . |
| 9 | Section IV. Bidding Forms, Price Schedule 1.1.3.12 and Section VI, Item 4.19 | 2pcs of Control and Protection cubicles including necessary cabling and earthing in remote Shahumyan 2 substation are defined in the price schedule. In the technical specification is only described that a differential protection relay shall be considered at Shahumyan 2. Please clarify if the differential protection relays shall be supplied loose or if a separate panel is to be considered. | Lot 1 | 2 pcs of cubicles should be supplied, which should be equipped with differential protection relay and control device. |
| 10 | SLD – CT’s at Autotransformer | SLD – CT’s at Autotransformer - There are CT’s indicated on the HV, MV and LV side of the Autotransformers. They are nowhere described nor listed in the Price schedule. Please clarify. | Lot 1 | Mentioned CTs are built-in CTs, which are accounted with transformers. |
| 11 | Appendix 10 | Appendix 10 -110kV Charentsavan-3 substation single line diagram Ц to realize - There are CT’s indicated on the HV, MV side of the Power transformers. They are nowhere described nor listed in the Price schedule. | Lot 2 | Mentioned CTs are built-in CTs, which are accounted with transformers. : |
| 12 |  | 220kV Circuit Breaker Autotransformer Feeder: - For Haghtanak the Circuit Breaker is described as: three phase circuit breaker - single pole operated; - For Ashnak the Circuit Breaker is described as: three phase circuit breaker - three pole operated - As per common practise the three pole operated type is used for Autotransformers. Please advise if the type of Breaker shall be considered as per the Specification or changed according to common practice. | Lot 1, 4 | As per specifications. |
| 13 | Section I, ITB, B. Preparation of Bids | Considering the amount documents to be prepared and printed, and also our experience from another tenders, we kindly ask you to confirm that some of the required documents like type test reports, equipment manuals and reference lists can be submitted in electronic form only, and in the paper copy of the offer there will be list with the documents and reference to them in the electronic form. | All | As per requirements mentioned in Bidding documents. |
| 14 | Section IV. Bidding Forms Schedule No. 1.Plant and Mandatory Spare Parts Supplied from Abroad 1.4 Mandatory Spare Parts Position 1.4.11.1 Protection & Control Relay of each type | Please kindly clarify what to be considered regarding the required quantity of 2 pieces: - each type of relay what is considered in the scope shall be supplied two times more as spare parts OR - Bidder defines two types of relays out of all relays considered in the scope and list them as spare part | All | 2 pcs of each type of main relays to be used should be supplied as a spare part. |
| 15 | Section IV. Bidding Forms Schedule No. 1.Plant and Mandatory Spare Parts Supplied from Abroad 1.4 Mandatory Spare Parts Positions 1.4.9.1, 1.4.9.2, 1.4.10.1, 1.4.10.2, 1.4.11.2 and 1.4.11.3 | Please kindly specify the quantities or advise if the Bidder can define them at its discretion | All | - 10 % of total quantity of each type of auxiliary relay to be used should be supplied as a spare part. - 10 % of total quantity of each type of lamps to be used should be supplied as a spare part. - 10 % of total quantity of each type of fuses to be used should be supplied as a spare part. - 5 % of total quantity of each type of mCBs to be used should be supplied as a spare part. |