## Sheet1
Rehabilitation of 220 kV "Haghtanak", 110 kV "Charentsavan-3", 110 kV "Vanadzor-1" and 220 kV "Ashnak" Substations ICB No: HV-W-ESRAF-1/2015
Item | Section | Document | Clause | Sub-Clause | Question | Reply
1 | IV | Price Schedule | Lot 1 - HAGHTANAK SS | Schedule No. 1. | Please clarify what is the requirement behind the item 1.3.1 Supply of GPS system. How is it different from the item 1.1.5.1 -one NTP server (Network Time Protocol) GPS signal distribution including the GPS antenna | NTP server (Network Time Protocol) is foreseen for time synchronization of all digital equipment and GPS system is for connection with satellite and correction of time.
2 | IV | Price Schedule | Lot 1 - HAGHTANAK SS | Schedule No. 1. | Please clarify what is the item 1.4.12.3 - Dynamometric switches for CB. Is it a position contact switch ?? | It is a key-switch for measurement of moment of the rotation.
3 | IV | Technical Data Sheet | 10kVPower Reactor - 40 MVA | N/A | Please clarify the type and rating of 10kV Power reactor to be installed in Haghtanak SS as the information given so far are not consistent: - part of the initial tender document, there is a technical specification for a 40MVA reactor outdoor, oil insulated with a current rating of 1025A - in the clarification No9, there is a short technical specification for a 40MVA reactor indoor with a current rating of 2500A. Please instruct what should be the current rating, if we can propose air insulated type, the installation (indoor /outdoor), the reactance (ohm/phase or % ) and rated short time current. Please clarify which Data Sheet should be included in our offer (the original one or the one includes in the clarification No 9?) | Please consider the data provided in Clarification N 9
4 | IV | Technical Data Sheet | 220kV and 110kV Disconnectors | Earth blade | It is required that earth blades on disconnectors should be motorized only for line earthing. Earth blades for disconnectors used for circuit breaker maintenance should only be manual. But line disconnectors have two earth blades; one toward the line and one toward the circuit breaker. Should we consider the two motorized or one manual (toward the CB) and one motorized (towar the line) | Earth blades should be manualy operated despite the blades quantity.