## Sheet1
Contract No. and Title: HV-W-ESRAF-1/2015
Sr. No. |  | Description | Question | Answer
1 | Sec. IV, Employers Requirement, Page No. 296, 322, 348 & 375 | Correct Altitude of all 4 locations. As per documents the same is not clear as mentioned below. 1. Haghtanak- < 1000mm 2. Charentsaran- > 1500mm 3. Vanadzor- < 1500mm 4. Ashnak- < 1600mm. | Please provide exact altitude parameters. | Please find the data in relevant Environmental management Plans.
2 | Sec. IV, Employers Requirement, Clause 1.1.6.1.6 page 302 and SLD for Haghtanak SS | 110 kV line bays - surge arresters is not mentioned/shown, whereas in price schedule of Haghtanak SS item no.1.1.3.6 shows Supply of 110 kV Surge arresters (1-p) - 12 Nos. | Please clarify what is to be considered. | As per SLD 110 kV surge arresters will be installed on busbars and 110 kV outputs of autotransformers.
3 | Sec. IV, Employers Requirement, Clause 1.1.11.1.3 & 1.1.11.1.4 page 327 & 328 and SLD for Charentsavan-3 SS | 110 kV line bays - surge arresters is not mentioned/shown, whereas in price schedule of Charentsavan-3 SS item no.1.1.1.6 shows Supply of 110 kV Surge arresters (1-p) - 13 Nos. | Please clarify what is to be considered. | As per SLD 110 kV surge arresters will be installed on busbars (3+3+1) and transformers inputs (3+3) .
4 | General | Detailed specifications for Heating and Air conditioning, Air extracting and Fire detection system is not provided in the tender documents. | Please provide the detail specifications. | Mentioned specifications should be specified at design stage as per technical norms.
5 | Sec. IV, Employers | Type of battery | Please provide the tupe of battery | As per General specifications of Bid documents
| Requirement clause | The batteries shall be: | required and Backup Time of
| 4.1 and Sub Clause 6, | 1. either of the sealed Lead-Acid type.; | Battery.
| Page No. 625 | 2. or of the Ni-Cd type.