## Лист1
Rehabilitation of 220 kV “Haghtanak”, 110 kV “Charentsavan‐3”, 110 kV “Vanadzor‐1” and 220 kV “Ashnak” Substations ICB No: HV‐W‐ESRAF‐1/2015
Item | Section | Document | Clause | Sub‐Clause | Question | Answer
1 | VI | Employers requirements | Haghtanak SS | 1.1.6.14.2 | Please clarify which type of power transformer fire fighting system is required; CO2 pulsed, electrical pump, diesel pump ? | Fire fighting system for power transformer is required to be water pulsed with electrical pump.
2 | VI | Employers requirement and clarification No10. Haghtanak SS | Energy meters. Haghtanak SS |  | Clarifications No10 ‐ line 106 states that the Energy Meter shoud be changed and Clarifications No10 ‐ line 110 states that only the cubicle should be changed. Please clarify. Please indicate the number of meters to be provided (or reinstalled) as the Section VI‐item 1.1.6.3.5 (p308‐309) states that feeder with client should be equipped. How many feeders will be connected to client? | In our Clarification N 10 - line 106 it was mentioned "It is requested to replace meters and foreseen cubicles" , which means that existing meters should be dismaltened from old cubicles and reinstall in new cubicles.
3 |  |  |  |  | Please provide the size of the following equipment. Fire-fighting system equipment and its channel, the size of the pool and the pump, the size of the waste treatment pool. And their location. | Water pool will be designed and calculated by Contractor according to the volume of oil of the equipment installed in the substation. The location of the pool will be determined in the design stage.