| No | Referance | Introduction | Question | Answer |
| --- | --- | --- | --- | --- |
| 1 | TECHNICAL SCHEDULE page 427 | Rated current of input cells and busbur coupler 6 kV – 2500 A Rated current of the transformer 40 MVA 110/6 kV at the SS Vanadzor 1 are 3700 A. | We think that Rated current of input cells and busbur coupler 6 kV at SS Vanadzor 1 should be higher than 2500 A. Please clarify. | Accept the values mentioned in Bidding documents. |
| 2 | TECHNICAL SCHEDULE page 450 | Rated current of input cells and busbur coupler 10 kV – 2500 A and outgoing – 630 A At the SS Vanadzor 1 each switchgear 10 kV have only two outgoing cells. | We think that Rated current of outgoing cells10 kV at SS Vanadzor 1 should be 1250 A. Please clarify. | Accept the values mentioned in Bidding documents. |
| 3 | TECHNICAL SCHEDULE page 455 | 10 kV Switchgear Number of trip coils- 2 Number of closing coil – 2 | If the protection for 10(6) kV cells are one unit why it is necessary to have two coils? Please clarify. | As it is mentioned in Bidding documents. |
| 4 | TECHNICAL SCHEDULE page 476 | 3 pole disconnector 110 kV Operating device – single pole | Please clarify in which SS and how many 3 pole disconnectors110 kV with single pole are necessary. | In particular spesifications of substations the specifications of bays are mentioned . |
| 5 | TECHNICAL SCHEDULE page 483 | Combinated disconnector and Earthing - 110 kV Earth blades – motorized operated | Please clarify in which SS and how many disconnectors110 kV with motorized operated earth blades are necessary. | It is mentioned in particular specifications. |
| 6 | TECHNICAL SCHEDULE page 512 | Three phase circuit Breaker 220 kV Action of CB operating mechanism – Three pole | We think that operating mechanism should be one pole. Please clarify. | It is mentioned in particular specifications. |
| 7 | TECHNICAL SCHEDULE page 524 | Combinated disconnector and Earthing - 220 kV Earth blades – motorized operated | Please clarify in which SS and how many disconnectors 220 kV with motorized operated earth blades are necessary. | It is mentioned in particular specifications. |
| 8 | TECHNICAL SCHEDULE page 537 | Three phase Disconnector 220 kV Action of DS operating mechanism – single pole | Please clarify in which SS and how many dissconnectors 220 kV with single pole operating mechanizm are necessary. | It is mentioned in particular specifications. |
| 9 | TECHNICAL SCHEDULE page 539 | The same | The same | It is mentioned in particular specifications. |
| 10 | Employer requirements page 330, TECHNICAL SCHEDULE page 501 | On page 330 it is mentioned 110 kV VT with 2 secondary windings. Same is shown on the SLD, but on page 501 it is mentioned 110 kV VT with 3 secondary windings | Please clarify how many secondary winding should have 110 kV VT. | As per particular specifications. |
| 11 |  | Same for 220 kV VT | Please clarify how many secondary winding should have 220 kV VT. | As per particular specifications. |
| 12 |  | Same for 10(6) kV VT | Please clarify how many secondary winding should have 10(6) kV VT. | As per particular specifications. |
| 13 | Employer requirements page 299 | Point 1.1.3.3.4 Outdoor 110 kV substation One (1) busbur measurement bay | We think it should be two (2). Please clarify. | Vide the item 1.1.6.1.9 on page 303. |
| 14 | Employer requirements page 308 | Point 1.1.6.3.5 Energy metering A multifunction energy meters shall be provided | We think that should be supply multifunction energy meters only for new 4 OHL 110 kV. Please clarify. | It is necessary to foreseen the supply and installation of connecting cables and cubicles for energy meters. Meters should not be supplied. |
| 15 | Employer requirements page 308 | Point 1.1.6.14.2 Description Installation of fire protection gates. | Please clarify what is “fire protection gates”. | It means Emergency Exit . |
| 16 | Employer requirements page 324 | Point 1.1.8.3.3 Outdoor 110 kV substation Two (2) voltage busbur | We think it should be two (2) voltage busbur and transfer busbur. Please clarify. | I would kindly ask you to study particular specifications attentively. |
| 17 | Employer requirements page 336 | Point 1.0.11.5.2 Telecommunication | First two points equipment are not installed at SS Charentsavan 3. Please clarify. | In Charentsavan -3 and Vanadzor-1 SS there are no any RTU, but it should be foreseen Gateways. |
| 18 | Employer requirements page 354 | Point 1.1.13.7.6 110 kV busburs - Busbur with flexible conductors | We should replace busbur with flexible conductors only at the part where we are installing new equipment? Please clarify. | Please vide item 1.1.1.12 (page 121) and item 1.1.1.12 (page 144). |
| 19 | Employer requirements page 360 | Point 1.1.13.9.9 6 kV equipment technical data sheet … and its RTU equipment ….. | At SS Vanadzor 1 there are no RTU. Please clarify. | It is not necessary . |
| 20 | Employer requirements page 362 |  | All three points equipments are not installed at SS Vanadzor 1. Please clarify. | It should be foreseen Gateways on Vanadzor-1 SS. |
| 21 | Employer requirements page 371 | Point 1.1.13.27.1 General FAT for power transformers | At SS Vanadzor 1 we haven’t supplied power transformer. Please clarify - we should organize FAT for power transformer - In which point of price schedules we should put the prices for FAT for each SS? | - For the equipment to be repaired it is not foreseen any FAT. - It is appropriate to include the cost of FAT in the cost of equipment to be supplied. |
| 22 | Employer requirements page 378 | Point 1.1.14.3.3 Outdoor 220 kV substation Two (2) voltage busbur | We think it should be two (2) voltage busbur and transfer busbur. Please clarify. | Vide item 1.1.17.1. 8 (page 383) of particular specification. |
| 23 | Employer requirements page 378 | Point 1.1.14.3.4 Outdoor 110 kV substation Two (2) voltage busbur | We think it should be two (2) voltage busbur and transfer busbur. Please clarify. | Vide item 1.1.17.1. 14 (page 385) of particular specification. |
| 24 | Employer requirements page 386 | Point 1.1.17.1.16 Transformers | Nothing is mentioned about the volumes of repairing of the boots transformer. Please provide the volumes. | It should be implemented in the same volumes as it is mentioned in item 1.1.17.1.16 (page 386). |
| 25 | Bidding Forms Page 75 | Supply of Autotransformer 125MVA 220/110/10kV including transformer monitoring system, necessary steel structure cabling and earthing | Please give the detail description for the monitoring system and its technical specification. | Installation of new monitoring and diagnostic system including : - Phase current A,B,C outgoing socket pin, - Tangents of phase A,B,C (%), - Shifting of phase A,B,C (degree), - Phase imbalance, - Phase capacitance (picofarad), - Partial discharge - Earthing (impulse/s), - Neutral (impulse/s), - Bushings 110/220 kV phase A,B,C - Humidity of environment (%), - Temperature of environment Co - Temperature of upper part of cooling Co, - Temperature inside device Co. |