## Лист1
| Question | Reply
1 | Regarding to the Short circuit impedance for the 63MVA Transformer in the substation Ashnak-1, the technical data sheet request Primary/Tertiary is 10% (Page 556), and the load loss is ≤120, it is not a normal technical request for the transformer. At the same time, the impedance data indicate in the nameplate of exiting transformer are Primary/Secondary 10% and Primary/Tertiary 35%, we believe this data is reasonable impedance, so please recheck it and give us clarification. | For the tecnical specification of 63 MVA autotransformer to be supplied on Ashnak SS regarding the Short circuit voltage instead of mentioned it should be consider as follows: Primary/Secondary- 10%, Primary/Tertiary- 35%, Secondary/Tertiary- 21% and the load loss is ≤180.
2 | To eliminate the ambiguity in the preparation of the Bid you confirm that the rules of overheating will be the following: a) the winding temperature rise over the air: 55K; b) the upper oil layer temperature rise over the air: 50K; c) winding <hot spot> temperature rise over the air: 68K; | As per Bidding documents
3 | 63 MVA autotransformer on Ashnak SS. Can you confirm that the Bid should be prepared for AT with parameters as an existing AT | The power of tertiary winding consider as 15/25/32, The voltage regulation should be done from middle voltage side (110 kV)- rate of regulation ±8x1.5%, HV- 230 kV, MV- 121 kV, Short circuit voltages vide in item 1
4 | Please confirm that the value of short-circuit losses ≤120 kW specified in Item 8 of the «Technical Shedule -Main data» consider the power ONAN (42 MVA), since for AT63MVA it is a very small quantity | vide in item 1
5 | прошу согласовать следующие величины испытательных напряжений внутренней изоляции нового АТ63МВА: - Линия ВН: ПГИ- 750кВ; КПЧ индуктированное (кратковременное промышленной частоты)- 325кВ - Линия СН: ПГИ- 480кВ; КПЧ индуктированное (кратковременное промышленной частоты)- , - Общая нейтраль автотрансформатора: КПЧ приложенное (кратковременное промышленной частоты)- 85кВ. 200кВ. please agree on the following values of the test voltage internal insulation of the new AT 63 MVA - line HV: PGI- 750KV; SCF the induction (short-term commercial frequency) - 325kV - line MV: PGI- 480kV; SCF the induction (short-term commercial frequency) - - Total autotransformer neutral: SCF applied (short-term commercial frequency) - 85kV. 200kV. | Vide Clarification 13 items 5,6,7 and last item of this questionaire.
6 | Также прошу подтвердить возможность ограничения мощности нового автотрансформатора на отпайке ниже "минус 4х1,5%", так как такое же ограничение имеется у существующего на объекте автотрансформатора. Это позволит выбрать ПУ РПН на меньший ток и соответственно, оно будет меньше стоить, что отразится на цене автотрансформатора. Also, please confirm the possibility of limiting the power of the new transformer in the sealing-off below the "minus 4x1,5%", since the same restriction has an existing on-site auto-transformer. This will select the position of tap changer at less current and therefore, it will cost less and that reflected in the price of the autotransformer. | It is not acceplatble.
7 | For 125 MVA Autotransformer in Haghtanak SS Offered by bidder: Short circuit impedance at the rated power of 125 MVA for all the taps of the OLTC HV-MV - Primary / Secondary % 12 - Primary / Tertiary % 40 - Secondary / Tertiary % 23 - Tolerances (on measured values) % according IEC | For 125 MVA AT on Haghtanak SS It is neccessary to consider the following data. Primary/Secondary- 10%, Primary/Tertiary- 35%, Secondary/Tertiary- 21% The voltage regulation should be done from middle voltage side (110 kV)
8 | In «Technical Shedule -Main data» (item 6, p.566) the wrong «Vector group» is specified. Vector group shall be as follows: YNa0d11. Please confirm. | Please vide iten 4 in Clarification 6.
9 | In the «Technical Shedule –Main data» the test voltages of the internal insulation of autotransformer’s common neutral are not specified. Please confirm the data proposed by the designers of Bidder: For Autotransformer 125 MVA: 85 kV (AC, applied). | It is acceptable
п.6 Vector group | D,d4, при этом в документе Clarification № 13 (ответы заказчика на вопросы конкурентов) указана схема Y-Y-0. Приемлима Схема соединения согласно Appendix 1? Mentioned D,d4, at the same time in the Clarification № 13 it is noted the scheme Y-Y-0. Is it applicable the connection scheme as per our Appendix 1? | Attached it is enclosed the proposed scheme of connection of windings in boost transformer and the outputs arrangements.
п.10 Short-circuit impedance | Short-circuit impedance at the rated power of 40 MVA for all the taps of the OLTC – 10% Is it applicable for the position 1 – 10,0% and position 21 – 8,0%? | As per bidding documets.