## Sheet1
Construction of New 400kV Kunene Substation and Omatando 400/132kV Substation Extensions
Tender No. NPWR/2015/50
Sr. Nos. | Clause nos/ Clause Name | Query | Reply
9 | General | We presume the oil of dismantled transformer will be stored in oil drums provided by HVEN. Please confirm. | The oil from dismantled transformers of Haghtanak SS should be replaced and stored in "Shahumyan-2" SS oil tanks. The oil from dismantled transformers of "Charentsavan- 3" SS should be stored in oil tanks after their rehabilitation. The oil from dismantled transformers of "Ashnak" SS should be stored in oil tanks located in the substation after their rehabilitation.
10 | Section VI Employer's requirment ,clause 1.2.4.7.1.1 | The telecommunications system includes: • a network of fibres optic cables on HV-lines (OPGW) between substations We preume the laying of OPGW between substations is not included in the present scope of work. Please confirm. | Yes.
220 / 110 / 10 kV Haghtanak Substation
1 | General | It has been mentioned that the existing substation is to be rehabilitated . however it seems that the complete substation on 220 kV side is to be rehabilitated as seen from the BOM . Pl confirm if is it correct . | Yes.
2 | Single Line Diagram scheme | The revised SLD with ring main arrangement does not clarify how the line and the transformer will be protected at same time since the same common CT is being used for both the line and the transformer . Pl clarify | The protection shall be supplied from the different cores of the same current transformer. Line and transformer shall have different protections.
3 | Booster transformer | Since the 10/10 kV boost transformer and the 10 kV reactor are in series , the charging current for booster transformer will be very high. Pl clarify | As per Bidding documents
4 | 10 kV reactor | Pl clarify purpose of providing the 10 kV reactor in series with booster transformer . It is not seen in the BOM of 10 kV feeders and also Purpose of providing the same. | As per Bidding documents and the supply of reactor vide on page 75 item 1.1.2.3..
5 | 10 kV Reactor | The reactor rating is also not mentioned anywhere nor in the SLD nor any technical particulars are given . Please provide the same | Please Vide the Clarification 9.
6 | CTs near Transformer | Current transformers are shown on 220 /110 and 10 kV side of the Autotransformer in the proposed SLD . Are these bushing CTs or external CTs in addition to the CTs on the main feeders of respective voltage level. Please clarify. | These are the current transformers built-in autotransformers.
7 | Tertiary rating | The rating of the 10 kV winding of the 220/110/10 kV transformer given as 40/40/63 . The booster transformer rating connected to the tertiary is 40 MVA . There is mismatch. Pl clarify | As per Bidding documents .
8 | Current transformers | The CT secondary current is mentioned as 5 A and that is why the burdens are as high as 50 VA to cater for longer lead length . Generally for outdoor SS CTs the secondary current is kept at 1A and that is standard practice . Pl confirm | As per Bidding documents .
9 | Ring main distribution | Because all the four Feeders on the 220 kV side are to be rehabilitated , we feel the feed for second line or transformer will not be available when the outage is taken on the other transformer . this is a double contingency and will keep the substation out of power when fault occurs on the healthy feeder in the shut down period .Please clarify . | The clarification will be made later .
10 | Existing foundations | Since all the equipments in the bay are to be replaced , can we use the existing civil foundations , wherever possible , by modifying them to reduce the shutdown time . Pl confirm | No .
11 | Line trap on 110 kV feeders | It is specified that the 110 kV line trap will be supplied by client and the new supplied CVT should match with this line trap . that means the line trap to be mounted on CVT . This is little difficult as the existing line traps are of old design . It is recommended to mount line trap on separate structures or hanging from the gantries for easiness and convenience . Pl confirm | Please Vide item 1 of Clarification 13.
12 | Earthing Switch Motorised | The earthing switch is proposed to be motor operated . Normally the earthswitch is to be operated when desired . hence it is always interlocked electrically and mechanically with its respective main switch or other switches . circuit breakers . If the electrical interlock fails due to loose wiring or other reasons and if the earth switch gets closed electrically by mistake , then it is very hazardous and it will be closing on live portion . It is therefore recommended that the ES closing should be only intentional and hence mechanical only . Pl consider and confirm . | As per Bidding documents .
“ 110 / 10 kV CHARENTSAWAN “ SUBSTATION
Charentsawan 110 kV
1 | Charentsawan 110 kV | What is the purpose of providing 1 set of either side of the CB in the existing layout. Do you expect the arrangement after modifications. | The question is not clear.
2 | Proposed SLD Appendix 10 | The transformer is shown with bushing mounted CT in SLD . Pl confirm what are CTs shown on either side of transformer in SLD. | These are the current transformers built-in autotransformers.
3 | Proposed SLD Appendix 10 | What is the voltage rating of the surge arrestor on the neutral of 110 kV side of transformer . the voltage at neutral will not be 110 kV , hence SA for that rating will not function properly . Please specify rating of SA. | As per Bidding documents .
4 | Proposed SLD Appendix 10 | No Voltage transformer is shown on the secondary side of transformer . What voltage will be sensed by the tap changer. This is seen for secondary’s for all transformer at all substations . | As per Bidding documents .
5 | Proposed SLD Appendix 10 | On 110 kV line , the line traps and CVTs are not shown for each feeders . But are shown randomly . Please confirm whether the line traps and CVT are to be provided only to the Line feeder in which they are shown. | As per Bidding documents .
6 | Proposed SLD Appendix 10, 110 kV Line trap | It is specified that the 110 kV line trap will be supplied by client and the new supplied CVT should match with this line trap . that means the line trap to be mounted on CVT . This is little difficult as the existing line traps are of old design . It is recommended to mount line trap on separate structures or gantries for easiness and convenience . pl confirm . | As per Bidding documents and vide item N 1 of Clarification 13.
7 | Proposed SLD Appendix 10 | No equipments are shown in the proposed SLD for line feeders Zangu 1 & 2 and Lusavan 1 & 2 . Pl confirm whether any equipments Line trap , CVT , SA are required or not. | As per Bidding documents .
8 | Proposed SLD Appendix 10, Disconnector on neutral ES | The disconnector is shown on the neutral of the 110 kV side of transformer . Since the neutral is solidly grounded and if by mistake the disonnector is kept open and neutral will remain floating and the protection will be jeopardized in that case .Please confirm whether we can provide manual diconnector. | As per Bidding documents .
9 | Earthing Switch Motorised | The earthing switch is proposed to be motor operated . Normally the earth switch is to be operated when desired . hence it is always interlocked electrically and mechanically with its respective main switch or other switches . circuit breakers . If the electrical interlock fails due to loose wiring or other reasons and if the earth switch gets closed electrically by mistake , then it is very hazardous and it will be closing on live portion . It is therefore recommended that the ES closing should be only intentional and hence mechanical only . Pl consider and confirm . | As per Bidding documents .
10 | Existing SLD and layout | The layout and existing SLD do not match with each other . All 110 kV , 8 outgoing feeders are shown on one side where as in the layout 2 feeders are shown going on the other side . This calls for additional gantries . Hence the orientation of the line feeders is important . Please clarify. | The actually existing arrangement will remain.
11 | Existing SLD and layout | In continuation to above gantry strctures are required for feeders Taran , Solak , Oaxsi 1 and 2, and Lusavan 1and 2 . Pl confirm | The existing portals will used.