High Voltage Electric Networks CJSC

Rehabilitation of 220 kV “Haghtanak”, 110 kV “Charentsavan-3”, 110 kV “Vanadzor-1” and 220 kV “Ashnak” Substations

| Item No. | Tender Document Ref. | Query | Applies to (S/S or Lot) |
| --- | --- | --- | --- |
| 1 | HVEN Clarification No. 12: - Haghtanak S/S item no. 13 - Charentsavan S/S item no. 8 | For 6kV and 10kV outgoing cables, the scope includes cable up to the substation boundary. Please clarify if there shall be considered a termination at the boundary or if we shall consider additional loose cable quantity (if so, what length?) for future connection by others outside of the substation boundary. | Yes the cables connection should be implemented by Contructor outside the substation boundary. |
| 2 | According to chapter 4.17 “General technical specification – MV protection relays” on page 849 | It is specified that the protection relay also shall provide the control part of the bay (combi device). On the other hand we see in the communication architecture of the substations that control and protection is divided into two devices. How shall it be offered? | Protection relays will not implement the control function. Control will be implemented only by control devices. |
| 3 | S/S Vanadzor | There is no 110kV distance protection and 110kV busbar protection specified in the tender document. The document “Price schedules.docx” includes in Lot 3 the postions 1.1.1.10 and 1.1.1.11 referring to the functionality. Shall we consider that in the offer? If yes, please specify if we need distance protection or line differential protection. | In item 1.1.1.11 it is mentioned the quantity – 0. The protection is foreseen only for transformer and Bus coupler on the 110 kV side. |
| 4 | S/S Haghatanak | According to tender documents no 220kV BBP is defined but in document price schedule there is point 1.1.1.10 mentioning the BBP. Shall we consider this in our offer? If yes, please specify functionality. | Busbar Protection is not necessary In the 220 kV side of Haghtanak SS. |
| 5 | S/S Charentsavan | Power Transformers 110/10kV 25MVA: - please confirm if the location of the regulation will be done at the end of the primary winding - Should uniform or non-uniform insulation be considered? | Yes Question is not clear |
| 6 | S/S Haghatanak | Autotransformers 220/110/10kV 125MVA: - please clarify if the short-circuit impedance in the pair Primary/ Tertiary is 10% in 125 MVA base. | For the Technical specifications of 125 MVA AT on page 567 is should be considered the follows. Primary/ Tertiary is 10%, Primary/Secondary – 35%, Secondary/ Tertiary - 21%, |
| 7 | S/S Ashnak | Autotransformer 220/110/10kV 63MVA: - please clarify if the short-circuit impedance in the pair Primary/ Tertiary is 10% in 63 MVA base. | For the tecnical specification of 63 MVA autotransformer to be supplied on Ashnak SS (page 556) regarding the Short circuit voltage instead of mentioned it should be consider as follows: Primary/Secondary- 10%, Primary/Tertiary- 35%, Secondary/Tertiary- 21% and the load loss is ≤180. |
| 8 |  | We kindly ask you to provide the aproximate scope of works regarding the water supply and drainage systems in 4 substations. | 1. In Charentsavan -3 substation the existing sewarage system will be used. The water supply should be implemented from the pipe which is at the distance of aproximately 1 km from the substation boundary. Construction of internal water supply system. 2. In Haghtanak substation the existing sewarage system will be used. Reconstruction of internal water supply system. 3. In Ashnak substation the existing sewarage system will be used, but aproximatelly 50 m is a subject of replacemet. The water supply should be implemented by new pipe from the distance of aproximately 40 m from the substation boundary. Reconstruction of internal water supply system. 4. In Vanadzor substation the water supply should be implemented by new pipe from the distance of aproximately 40 m from the substation boundary. Reconstruction of internal water supply system. The existing sewarage system will be used with replacemet of aproximatelly 50 m . |