## Лист1
Rehabilitation of 220 kV “Haghtanak”, 110 kV “Charentsavan‐3”, 110 kV “Vanadzor‐1” and 220 kV “Ashnak” Substations ICB No: HV‐W‐ESRAF‐1/2015 |  |  |  | 23/10/2015 ‐ Rev 0
Item | Section | Document | Clause | Sub‐Clause | Question
1 | IV | Price Schedule | N/A | N/A | Please provide Price Schedule in an editable excel file | As per WB requirments bidding document has been prepared in PDF and MS Word formats.
2 | Appendix | Appendix 3‐Layout of Haghtanak | N/A | N/A | We did not find the layout of the final stage of the substation. Please clarify if the document is missing or if it is the contractor responsibility to design and propose a layout | The final layout sould be prepared by contractor.
3 | VI | Haghtanak SS | N/A | N/A | We assumed that part of the substation should be kept live during the works. Please confirm Has the Employer already prepare a sequence of works or is it the contractor responsibility to propose? Please indicate policy regarding outage duration , | Outages should be implemented stage by stage. Contractor should submit the proposal regarding the outaged and stages.
[5 empty] | please clarify procedure and ownership concerning dismantled material . | In Haghtanak SS all dismantled equipment should be removed to Shahumyan-2 SS - aprox 3 km. In Ashnak and Charentsavan-3 substations dismantled equipment should be stored at the same substations in previosly prepared temporary open storages. In Vanadzor-1 SS dismantled equipment should be stored at substation area.
4 | VI | Technical Data Sheet | ATR 220/110/10kV ‐ 125MVA | N/A | In the 220/110/10kV ‐ 125 MVA transfomer data sheet. It is mentioned that this is a ATR even if the declared connection group “YNyn0d11” is typical for TR. Please clarify whether the 125 MVA is ATR or TR. If this is a ATR, please confirm vector group | It is Autotransformer 125 MVA and connection group is "YN avto d11" .
5 | VI | Technical Data Sheet | ATR 220/110/10kV ‐ 125MVA | N/A | In the 220/110/10kV ‐ 125 MVA transformer data sheet, it is requested power for the primary and secondary winding to be 60/90/125 MVA ONAN/ONAF1/ONAF2 corresponding to 48%ONAN‐72%ONAF1‐100%ONAF2. In keeping the same percentage on the different cooling stage on the tertiary winding we should have 30/45/63 MVA ONAN/ONAF1/ONAF2 that is not in line with what is mentioned in the same data sheet (40/50/63). Please so confirm the possibility to modify the rated power on the tertiary winding to 30/45/63 MVA | We have no objection. The same percentage rate should be maintained.
6 | VI | Technical Data Sheet | ATR 220/110/10kV ‐ 125MVA | N/A | In the 125 MVA transformer data sheet the insulation levels should be in compliance with IEC standard as mentioned. According to these Standards, the rated voltage levels corresponding to their requests are 245kV and 123kV respectively for primary and secondary winding. Please confirm the possibility to consider these Standards values instead of the 252kV and 26kV indicated in the same document | The proposal is acceptable.
7 | VI | Technical Data Sheet | ATR 220/110/10kV ‐ 125MVA | N/A | Regarding lossese of the 220/110/10kV transfromer; it is requested a maximum load losses value of 230kW. Please clearly mention to which volta ge ratio and to which ppower this losses limit makes reference | The load losses value of 230kW considered for rate voltage and power.