## Лист1
No.: | Date | Refernce (Lot, Document, chapter,page) | Issue | Question Bidder | Answer Employer
Clarif. No. 1 sent 20/10/2015 (click on cross to open)
1 | 2015-10-20 | "ICB_4 Substations_HVEN_04.09.15.pdf" Page 295/1036 Chapter 1.1.2.7.1 (General) | Training | “Training for overhead lines” We will not be responsible for OHLs. We assume not to do related training.
2 | 2015-10-20 | "ICB_4 Substations_HVEN_04.09.15.pdf" Page 349/1036 (Vanadzo-1) | Trafo repair | Requirement: two (2) Transformers 110/10 kV 40 MVA to rehabilitate; two (2) Transformers 110/6 kV 40 MVA to rehabilitate; For evaluation of current transformer conditions we need the following: - Manufacturer - Manufacturer- / commissioning date - technical data (rating plate) - PD-measurement / analyze - oil in gas analysis - failure suffered by the transformer
3 | 2015-10-20 | "ICB_4 Substations_HVEN_04.09.15.pdf" Page 377/1036 (Ashnak) | Trafo repair | Requirement: one (1) Autotransformer 220/110/10 kV 63 MVA to repair; two (2) Boost transformers 10/10 kV 40 MVA to repair; Repairing and painting with anti-corrosion paint of existing House transformers 10/0.4 kV 630 kVA; For evaluation of current transformer conditions we need the following: - Manufacturer - Manufacturer- / commissioning date - technical data (rating plate) - PD-measurement / analyze - oil in gas analysis - failure suffered by the transformer
4 | 2015-10-20 | General question / all lots | Drawings | In order to do proper determination of scope and to find the best technical solution we need following as build drawings from existing substations: 1. Building 2. Drainage / sewerage system 3. Cable routes 4. Layouts, sections 5. Foundation plan We need from the layouts / sections the workable files *.dwg for example or other format in order to implement new equipment.
5 | 2015-10-20 | General question / all lots | Workable docs | We need for tender preparation we need following documents in workable files: 1. Price lists as *.xls
6 | 2015-10-20 | General question / all lots | Tender docs in Armenian | Please send us the tender documentation in Armenian.
7 | 2015-10-20 | "ICB_4 Substations_HVEN_04.09.15.pdf" Page 476/1036 Data sheet 110 kV disconnector | Operating device 110 kV disconnector | Operating device for 110 kV disconnector "single pole" requested. Could we offer instead of "single pole" "three pole" devices - means one drive for all three poles? In substations Vanadzor-1 and Allaverdi-2 three pole devices are installed. Devices will be cheaper and cabling also.
8 | 2015-10-20 | General question / all lots | Soil investigation | For the existing substations we need the soil investigation reports.
Clarif. No. 2 sent 23/10/2015
9 | 2015-10-23 | "ICB_4 Substations_HVEN_04.09.15.pdf" Page 33 and 37/1036 ITB 11.1(k), ITB 21.1 | documentation-format | In ITB 11.1 (k) is requested submission of price list in MS-Word format and in ITB 21.1 MS-Excell. Please confirm MS-Excell as format for price lists. | As per ITB 21.1 Bidder should submit Price Schedule in MS -Ecell format.
10 | 2015-10-23 | "ICB_4 Substations_HVEN_04.09.15.pdf" Page 37 and 37/1036 ITB 21.1 | Doffer documentation | Requested offer documentation comprises of one original and three copies. As the postqualification documents nearly the same for each lot - please confirm that documents valid for all lots can be submitted in one original and three copies for all lots together (one time only) and not for each lot separately. | We confirm that documents valid for all lots can be submitted in one original and three copies for all lots together (one time only).
11 | 2015-10-23 | "ICB_4 Substations_HVEN_04.09.15.pdf" Page 316/1036 and "Appendix 8 -220kV Haghtanak substation Ц Environmental Management Plan.pdf" page 4/19 | refurbishment / new construction of control building | In mentioned documents are contradiction concerning new construction or refurbishment of control building. Please confirm that refurbishment is requested. | The requirements mentioned in particular specifications should be considered as a base.
12 | 2015-10-23 | General question / all lots "ICB_4 Substations_HVEN_04.09.15.pdf" | Workable docs | We need for tender preparation we need following documents in workable files: 1. Tender as *.doc (not available on submitted CD) for filling the requested information in Forms and Technical Schedules. | Technical Schedules are submitting in MS Word format.
13 | 2015-10-23 | "ICB_4 Substations_HVEN_04.09.15.pdf" Page 316/1036 and "Appendix 8 -220kV Haghtanak substation Ц Environmental Management Plan.pdf" page 4/19 | Ambient temperature | In mentioned documents are contradiction concerning ambient temperature: -35°C - + 50°C and -28°C-42°C (Environmental Management Plan). Please confirm temperature range -28°C up to 42°C as indicated in the Environmental Management plan. | Temperatures mentioned in Particular Specifications should be considered.
14 | 2015-10-23 | "ICB_4 Substations_HVEN_04.09.15.pdf" Pagees 556-569/1036 | Technical Schedules | Technical Schedules for Auto-transformers contains unreadable characters: a) Page 556 item 8 - b) Page 558 item 6 - c) Page 567 item 8 - d) Page 569 item 6 - Please send us current file with readable characters. | Technical Schedules for Auto-transformers 63 MVA and 125 MVA contains unreadable characters on following pages a) Page 556 item 8 - b) Page 558 item 6 c) Page 567 item 8 - d) Page 569 item 6 - It should be cosidered as Follows "Load loss between "very" HV and HV at rated power of 63 MVA and at average tempetarure of the windings of 75oC". The same respectivly should be considered for AT 125 MVA.