Technical schedules

| TECHNICAL SCHEDULE – Main Data |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Phase Surge Arrester - 6kV |  |  |  |  |  |
| Description |  |  | Units | Imposed Values | Guaranteed Values |
|  | 1. General characteristics |  |  |  |  |
|  | • Manufacturer |  |  | Specify |  |
|  | • Type |  |  | Specify |  |
|  | • Installation |  |  | Outdoor |  |
|  | • Housing (porcelain, polymer) |  |  | Brown Porcelain |  |
|  | • Minimum phase creepage distance |  | mm/kV | 31 |  |
|  | 2. Electrical characteristics |  |  |  |  |
|  | • Rated frequency (fr) |  | Hz | 50 |  |
|  | • Network nominal voltage |  | kV | 6 |  |
|  | • Maximum service voltage (Um) |  | kV | 7,2 |  |
|  | • Nominal discharge current |  | kA peak | 10 |  |
|  | • Continuous Operating Voltage (Uc - COV) |  | kV | 4.5 |  |
|  | • Insulation level for the housing |  |  |  |  |
|  | - Power frequency withstand voltage 50Hz - 1 min. forthe housing |  | kV | 20 |  |
|  | - Lightning Impulse withstand voltage (1,2/50µs) for the housing |  | kV | 60 |  |

| TECHNICAL SCHEDULE – Data for Information |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Phase Surge Arrester - 6kV |  |  |  |  |  |
| Description |  |  | Units | Imposed Values | Guaranteed Values |
|  | 1. General characteristics |  |  |  |  |
|  | •Place of manufacture |  |  | Specify |  |
|  | • Standards |  |  | IEC |  |
|  | • Construction type |  |  | MO (metal oxide) |  |
|  | • Model |  |  | Specify |  |
|  | • Surge counter |  |  | Yes |  |
|  | -number |  |  | 1 by phase |  |
|  | -type |  |  | Specify |  |
|  | 2. Normal service conditions(please refer to the site conditions of each substation) |  |  |  |  |
|  | • Ambient temperature range |  | °C |  |  |
|  | • Relative humidity |  | % |  |  |
|  | • Maximum altitude |  | m |  |  |
|  | • Maximum ice coating |  | mm |  |  |
|  | • Maximum pressure of the wind speed |  | Pa |  |  |
|  | • Solar radiation |  | W/m² |  |  |
|  | 3. Electrical characteristics |  |  |  |  |
|  | • Surge arrester rated voltage (Ur) |  | kV | Specify |  |
|  | • Maximum temporary Over Voltage |  |  |  |  |
|  | - for 1 s |  | kV | Specify |  |
|  | - for 10 s |  | kV | Specify |  |
|  | • Maximum residual voltages for a lightning impulse 8/20 μs |  |  |  |  |
|  | - at I = 5 kA |  | kV peak | Specify |  |
|  | - at I = 10 kA |  | kV peak | Specify |  |
|  | - at I = 20 kA |  | kV peak | Specify |  |
|  | • Maximum residual voltages for a lightning impulse 30/... μs |  |  |  |  |
|  | - at I = 1 kA |  | kV peak | Specify |  |
|  | • Line discharge class (IEC 60099-4) |  |  | Specify |  |
|  | • Reference current and voltage |  | kV /mA | Specify |  |
|  | 4. Mechanical characteristics |  |  |  |  |
|  | • Pollution Class |  |  | outstanding (no pollution) |  |
|  | • Over-pressure valve |  |  | Yes/No |  |
|  | - type |  |  | Specify |  |
|  | - pressure relief capability |  | kA | ≥25 |  |
|  | • Maximum allowed strength (MPSL) |  | N | Specify |  |
|  | • Maximum dynamic allowed strength (MPDSL) |  | N | Specify |  |
|  | • Total height (including insulated base) |  | mm | Specify |  |
|  | • Total weight |  | kg | Specify |  |
|  | 5. Contruction details |  |  |  |  |
|  | • Type of line connection (Al, ...) |  |  | Specify |  |
|  | • Type of ground connection ( stainless steel, ….) |  |  | Specify |  |
|  | • Insulated base |  |  | Yes |  |
|  | • Guard ring (outer diameter) |  | mm | Specify |  |
|  | • Number of elementary columns |  |  | Specify |  |
|  | • Terminal for connection of online Leakage Current Measurement system |  |  | Yes |  |
|  | 6. Paint and corrosion protection |  |  |  |  |
|  | • Oxydable metal parts |  |  | hot dip galvanizing |  |
|  | • Screws, nuts, bolts,…. |  |  |  |  |
|  | - for diameter ≤ M16 stainless steel |  |  | Yes |  |
|  | - for diameter > M16 hot dip galvanized steel and painted |  |  | Yes |  |
|  | • Duplex principle (galvanized + paint) according GTS |  |  | Yes |  |
|  | • Final color paint |  |  |  |  |
|  | - pieces to earth |  |  | Specify |  |
|  | - live parts |  |  | Specify |  |
|  |  |  |  |  |  |
|  | 7. Testing |  |  |  |  |
|  | • Reports of type tests on similar equipment |  |  | Yes |  |
|  | • Routine test according to IEC 60099.4 |  |  | Yes |  |
|  | 8. Documents to be submitted |  |  |  |  |
|  | • Submital fase |  |  | 3 ex. |  |
|  | - General documentation |  |  |  |  |
|  | - List of references |  |  |  |  |
|  | - Type test reports |  |  |  |  |
|  | - datasheet completed |  |  |  |  |
|  | - dimensional drawing |  |  |  |  |
|  | • Ordering fase |  |  | 3 ex. |  |
|  | - erection instruction manual |  |  |  |  |
|  | - maintenance instruction manual |  |  |  |  |
|  | - static and dynamic efforts |  |  |  |  |
|  | - voltage curve at power-frequency in function of time |  |  |  |  |
|  | - drawings |  |  |  |  |
|  | - detailed dimensional drawing |  |  |  |  |
|  | - drawing of the rating plate |  |  |  |  |
|  | • Completed Manufactuer final report including |  |  | 3 ex. |  |
|  | - erection instruction manual |  |  |  |  |
|  | - maintenance instruction manual |  |  |  |  |
|  | - as built drawings |  |  |  |  |
|  | - voltage curve at power-frequency in function of time |  |  |  |  |
|  | - factory test report |  |  |  |  |
|  | 8. Languages |  |  |  |  |
|  | • All documents establish in English |  |  | Yes |  |

| TECHNICAL SCHEDULE – Main Data Air Insultated Switchgear AIS - 6 kV |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Description |  |  | Units | Imposed Values | Guaranteed Values |
|  | 1. General characteristics |  |  |  |  |
|  | • Manufacturer |  |  | Specify |  |
|  | • AIR Insulated metal-enclosed Switchgear (AIS) |  |  | Yes |  |
|  | • Indoor use |  |  | Yes |  |
|  | • Withdrawable Components |  |  | Yes |  |
|  | • Rated Maximum voltage (Ur) |  | kV | 7.2 |  |
|  | • Rated frequency (fr) |  | Hz | 50 |  |
|  | • Busbar system: Single, double |  |  | Single |  |
|  | • Method of earthing – Busbars side |  |  | Specify |  |
|  | • Method of earthing - Line side |  |  | Specify |  |
|  | • Busbars Segregated |  |  | Yes |  |
|  | • Material of cover and Portions |  |  | Metallic |  |
|  | • Material of Shutters |  |  | Metallic/earth |  |
|  | • Busbars and joints fully encapsulated |  |  | Yes |  |
|  | • Emergency manual trip facility (during failure of DC supply) |  |  | Yes |  |
|  | • Porcelain Color |  |  | Brown |  |
|  | 2. Rated Currents |  |  |  |  |
|  | • Rated currents |  |  |  |  |
|  | - Busbars |  | A | 2500 |  |
|  | - Incoming panel (transformer) |  | A | 2500 |  |
|  | - Busbar coupler |  | A | 2500 |  |
|  | - Outgoing panel (feeders) |  | A | 630 |  |
|  | • Rated short time withstand current (Ik) |  | kA | 25 |  |
|  | • Rated duration of short circuit (tk) |  | s | 3 |  |
|  | • Rated peak withstand current (Ip) |  | kA peak | 80 |  |
|  | 3. Rated voltage and rated insulation level |  |  |  |  |
|  | • Service voltage |  | kV | 6 |  |
|  | • Rated short duration power-frequency withstand voltage (AC) 1min-50Hz (Ud) – Phase to earth |  | kV | 20 |  |
|  | • Rated short duration power-frequency withstand voltage (AC) 1min-50Hz (Ud) – Across the isolating distance |  | kV | 25 |  |
|  | • Rated lightning impulse withstand voltage (1,2/50µs) (Up) – Phase to earth |  | kV | 60 |  |
|  | • Rated lightning impulse withstand voltage (1,2/50µs) (Up) – Across the isolating distance |  | kV | 70 |  |
|  | 4. Main Busbars |  |  |  |  |
|  | • material |  |  | Copper |  |
|  | • surface treatment (painted, insulated,….) |  |  | Silver plated copper |  |
|  | • Rated current at 50°C (corresponding to site rating) |  | A | 2500 |  |
|  | 5. Circuit Breaker |  |  |  |  |
|  | • Manufacturer |  |  | Specify |  |
|  | • Quenching fluid |  |  | Vacuum |  |
|  | • Withdrawable |  |  | Yes |  |
|  | • Fully encapsulated |  |  | Yes |  |
|  | • Rated maximum voltage (Ur) |  | kV | 7.2 |  |
|  | • Rated frequency (fr) |  | Hz | 50 |  |
|  | • Rated short duration power-frequency withstand voltage (AC) 1min-50Hz (Ud) – Phase to earth |  | kV | 20 |  |
|  | • Rated short duration power-frequency withstand voltage (AC) 1min-50Hz (Ud) – Across the isolating distance |  | kV | 25 |  |
|  | • Rated lightning impulse withstand voltage (1,2/50µs) (Up) – Phase to earth |  | kV | 60 |  |
|  | • Rated lightning impulse withstand voltage (1,2/50µs) (Up) – Across the isolating distance |  | kV | 70 |  |
|  | • Rated short circuit breaking current |  | kA | 25 |  |
|  | • Rated peak withstand current (Ip) |  | kA peak | 63 |  |
|  | • First-pole-to-clear-factor |  |  | 1.5 |  |
|  | • Rated Current |  |  |  |  |
|  | - Incoming panel (transformer) |  | A | 2500 |  |
|  | - Busbar Coupler |  | A | 2500 |  |
|  | - Outgoing panel (feeders) |  | A | 630 |  |
|  | • Operating sequence O-0,3s-CO-3min-CO |  |  | Yes |  |
|  | • Type of operating mechanism |  |  | 3 pole |  |
|  | • Manual spring discharge facility |  |  | Yes |  |
|  | • Type of power device |  |  | Motor – Spring |  |
|  | • Nominal control and operating voltage |  | V DC | 220 |  |
|  | • Nominal heater voltage |  | V AC | 220 |  |
|  | 6. Busbars disconnector or busbars switch |  |  |  |  |
|  | • Manufacturer |  |  | Specify |  |
|  | • Type |  |  | Specify |  |
|  | • Rated voltage (Ur) |  | kV | 7.2 |  |
|  | • Rated frequency (fr) |  | Hz | 50 |  |
|  | • Rated short duration power-frequency withstand voltage (AC) 1min-50Hz (Ud) – Phase to earth |  | kV | 20 |  |
|  | • Rated lightning impulse withstand voltage (1,2/50µs) (Up) – Phase to earth |  | kV | 60 |  |
|  | • Rated Current |  |  |  |  |
|  | - Busbar Coupler |  | A | 25000 |  |
|  | • Type of contact |  |  | Copper |  |
|  | 7. Making proof Earthing switch |  |  |  |  |
|  | • Manufacturer |  |  | Specify |  |
|  | • Type |  |  | Specify |  |
|  | • Rated voltage (Ur) |  | kV | 7.2 |  |
|  | • Rated frequency (fr) |  | Hz | 50 |  |
|  | • Rated short duration power-frequency withstand voltage (AC) 1min-50Hz (Ud) – Phase to earth |  | kV | 20 |  |
|  | • Rated lightning impulse withstand voltage (1,2/50µs) (Up) – Phase to earth |  | kV | 60 |  |
|  | • Rated short time withstand current (Ik) |  | kA | 25 |  |
|  | • Rated duration of short circuit (tk) |  | s | 3 |  |
|  | • Type of contact |  |  | Copper |  |
|  | 8. Current transformer |  |  |  |  |
|  | • Manufacturer |  |  | Specify |  |
|  | • Type |  |  | Cast Resin multicore, multi ratio, indoor |  |
|  | • Rated voltage (Ur) |  | kV | 7.2 |  |
|  | • Rated short duration power-frequency withstand voltage (AC) 1min-50Hz (Ud) – Phase to earth |  | kV | 20 |  |
|  | • Rated lightning impulse withstand voltage (1,2/50µs) (Up) – Phase to earth |  | kV | 60 |  |
|  | • Incoming Feeder |  |  |  |  |
|  | - Secondary Current |  | A | 1/1/5 |  |
|  | - Primary Current incoming / bus coupler |  | A | 1250-2500 |  |
|  | - Number of measuring cores |  |  | 1 |  |
|  | - Number of protection cores |  |  | 2 |  |
|  | • Outgoing Feeder |  |  |  |  |
|  | - Secondary Current |  | A | 1/5 |  |
|  | - Primary Current outgoing |  | A | 100-300-600 |  |
|  | - Number of measuring cores |  |  | 1 |  |
|  | - Number of protection cores |  |  | 1 |  |
|  | • For Earth-Fault relays |  |  |  |  |
|  | - Secondary Current |  | A | 1 |  |
|  | - Primary Current outgoing |  | A | 50 |  |
|  | - Number of protection cores |  |  | 1 |  |
|  | • Accuracy class rating and capacity of measuring core |  |  | 0.5/10 |  |
|  | • Accuracy class rating and capacity of measuring core |  |  | 10P20 |  |
|  | 9. Voltage transformer |  |  |  |  |
|  | • Manufacturer |  |  | Specify |  |
|  | • Type |  |  | Inductive cast resin single pole insulated |  |
|  | • Rated voltage (Ur) |  | kV | 7.2 |  |
|  | • Rated frequency (fr) |  | Hz | 50 |  |
|  | • Rated short duration power-frequency withstand voltage (AC) 1min-50Hz (Ud) – Phase to earth |  | kV | 20 |  |
|  | • Rated lightning impulse withstand voltage (1,2/50µs) (Up) – Phase to earth |  | kV | 60 |  |
|  | • Transformation Factor |  |  | 10000/√3 - 100/√3 - 100/√3 |  |
|  | • Accuracy class rating and capacity of measuring core and protection |  |  | 0.5/200 |  |
|  | • Accuracy class rating and capacity of metering core and protection |  |  | 0.2/60 |  |
|  | • Accuracy class protection |  |  | 3P |  |

| TECHNICAL SCHEDULE – Data for Information Air Insultated Switchgear AIS - 6 kV |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Description |  |  | Units | Imposed Values | Guaranteed Values |
|  | 1. General characteristics |  |  |  |  |
|  | • Place of manufacture |  |  | Specify |  |
|  | • Type |  |  | Specify |  |
|  | • Standards (last edition) |  |  | IEC 62271-200 |  |
|  | • Type of partitions (class PM or class PI) |  |  | PM |  |
|  | • Loss of service continuity classification |  |  | LSC2B |  |
|  | • Type of insulation |  |  | Air |  |
|  | • Internal Arc Classification (class IAC) |  |  | Yes |  |
|  | • Expected life of the switchgear |  | Years | Specify |  |
|  | 2. Operating conditions(please refer to the site conditions of each substation) |  |  |  |  |
|  | • Ambient temperature range |  | °C |  |  |
|  | • Relative humidity |  | % |  |  |
|  | • Maximum altitude |  | m |  |  |
|  | • Maximum ice coating |  | mm |  |  |
|  | • Maximum pressure of the wind speed |  | Pa |  |  |
|  | • Solar radiation |  | W/m² |  |  |
|  | • Vibrations due to external causes |  |  |  |  |
|  | 3. Rated Currents |  |  |  |  |
|  | • Temperature rise according IEC |  |  | Yes |  |
|  | • Circuit Breaker breaking capacity at Un |  | kA | 25 |  |
|  | •Internal Arc withstand Current (IAC) |  | kA - 1s | 25 |  |
|  | • IAC classification |  |  | AFLR |  |
|  | 4. Technical characteristics of the auxiliary circuits |  |  |  |  |
|  | • Rated voltage |  |  |  |  |
|  | - operating circuits, signalization, tripping, locking and motors |  | Vdc | 220 |  |
|  | - operating range |  | % | 85 to 110 |  |
|  | • Auxiliary contacts |  |  |  |  |
|  | - rated continuous current (class 1) |  | A | 10 |  |
|  | - rated capacity |  | A | 4A/220Vdc |  |
|  | 5. Main Busbars |  |  |  |  |
|  | • section |  | mm² | Specify |  |
|  | 6. Circuit Breaker |  |  |  |  |
|  | • Type |  |  | Specify |  |
|  | • Type of operating mechanism |  |  | Specify |  |
|  | • Manufacturer reference |  |  |  |  |
|  | • Type (energy) |  |  | Spring |  |
|  | • Energy |  |  | Mechanical |  |
|  | • On/Off push button for emergency |  |  |  |  |
|  | - electrical |  |  | No |  |
|  | - mechanical |  |  | Yes |  |
|  | • Mechanical position indicator |  |  | Yes |  |
|  | - CB On/Off |  |  | Yes |  |
|  | - Spring charged/discharged |  |  | Yes |  |
|  | • Operations counter |  |  | Yes |  |
|  | • Emergency crank for spring bending |  |  | Yes |  |
|  | • LV circuit: |  |  |  |  |
|  | • Number of trip coils |  |  |  |  |
|  | -Incoming panel |  |  | 2 |  |
|  | -Coupling panel |  |  | 2 |  |
|  | -Feeder panel |  |  | 2 |  |
|  | • Number of closing coils |  |  |  |  |
|  | -Incoming panel |  |  | 2 |  |
|  | -Coupling panel |  |  | 2 |  |
|  | -Feeder panel |  |  | 2 |  |
|  | • Number of undervoltage coils |  |  | 0 |  |
|  | • Interlocking coil for withdrawable CB only incoming panel |  |  | Yes |  |
|  | • Antipumping |  |  | Yes |  |
|  | • Auxiliary position contacts |  |  |  |  |
|  | - CB On/Off |  |  | 4NO+4NC |  |
|  | - CB on withdrawable position |  |  | 2NO+2NC |  |
|  | - CB spring charged/discharged |  |  | 1NO+1NC |  |
|  | 7. Busbars disconnector or busbars switch |  |  |  |  |
|  | • Type |  |  | Specify |  |
|  | • Type of operating mechanism |  |  | Specify |  |
|  | • Auxiliary position contacts |  |  | 4NO+4NC |  |
|  | • Mechanical position indicator |  |  | Yes |  |
|  | • Interlocking coil with push button |  |  | Yes |  |
|  | 8. Making proof Earthing switch |  |  |  |  |
|  | • Type |  |  | Specify |  |
|  | • Closing capacity (type: "high speed"closure) |  | kA peak | 63 |  |
|  | • Type of operating mechanism |  |  | Manual |  |
|  | • Auxiliary position contacts |  |  | 4NO+4NC |  |
|  | • Mechanical position indicator on command side |  |  | Yes |  |
|  | • Interlocking coil with push button |  |  | Yes |  |
|  | • Busbars VT will be withdrawable |  |  | Yes |  |
|  | 9. Safety interlocking |  |  |  |  |
|  | • Interlocking |  |  | Specify |  |
|  | - CB + access to MV parts and earthing-switch |  |  | Specify |  |
|  | - Standard manufacturer's interlocking |  |  | Yes |  |
|  | - Others solution |  |  | Specify |  |
|  | - BB disconnector or BB switch |  |  | N.A. |  |
|  | • Voltage system detector |  |  | Yes |  |
|  | - according IEC 61243 part 5 |  |  | Yes |  |
|  | - On MV cables |  |  | Yes |  |
|  | • Mimic diagram showing all devices positions |  |  | Yes |  |
|  | • Padlockable operating devices (BB switch, BB disconnector, earthing-switch,…) |  |  | Yes |  |
|  | • Visible position of BB switch, BB disconnector, earthing-switch via windows |  |  | Yes |  |
|  | • Mechanical interlock of earthing-switch in open/close positions |  |  | Yes |  |
|  | • Labeling (panels, BB, phases,….) |  |  | following GTS |  |
|  | 10. Enclosures |  |  |  |  |
|  | • Three phase enclosure |  |  |  |  |
|  | - at busbar level |  |  | Yes |  |
|  | - at panel level |  |  | Yes |  |
|  | • Used material |  |  | Specify |  |
|  | • IP degree |  |  | ≥32 |  |
|  | • thickness of the partitions |  | mm | Specify |  |
|  | • closure of the bottom of the panels by non-magnetic cut sheets for MV cables entry |  |  | Yes |  |
|  | 11. Cable compartment |  |  |  |  |
|  | • Possible connections on: |  |  |  |  |
|  | - Incoming transformer feeders |  |  | Specify |  |
|  | - Outgoing feeders |  |  | Specify |  |
|  | • Maximum cable diameter |  |  | Specify |  |
|  | • Standard facilities for cable testing |  |  | Specify |  |
|  | • Minimum number of cables and section |  |  | showing on drawings |  |
|  | 12. Dimensions |  |  |  |  |
|  | As applicable: |  |  |  |  |
|  | • Incoming panel |  |  |  |  |
|  | - width / length / height |  | mm | Specify |  |
|  | - weight |  | Kg | Specify |  |
|  | • Outgoing panel |  |  |  |  |
|  | - width / length / height |  | mm | Specify |  |
|  | - weight |  | Kg | Specify |  |
|  | • Bus coupler panel |  |  |  |  |
|  | - width / length / height |  | mm | Specify |  |
|  | - weight |  | Kg | Specify |  |
|  | • Busbar VT |  |  |  |  |
|  | - width / length / height |  | mm | Specify |  |
|  | - weight |  | Kg | Specify |  |
|  | • Bus earthing |  |  |  |  |
|  | - width / length / height |  | mm | Specify |  |
|  | - weight |  | Kg | Specify |  |
|  | • AIS room |  |  |  |  |
|  | - minimum space at front of the switchgear |  | mm | Specify |  |
|  | - minimum space at rear of the switchgear |  | mm | Specify |  |
|  | - minimum space at top of the switchgear |  | mm | Specify |  |
|  | - minimum space at side of the switchgear |  | mm | Specify |  |
|  | - minimum needed space for extension of the switchgear |  | mm | Specify |  |
|  | - minimum height, the switchgear will be with an exhaust duct connected outside the building |  | mm | Specify |  |
|  | • Height of connecting of the cable terminals from the ground level |  | mm | Specify |  |
|  | • Ground fixations |  |  | Specify |  |
|  | • LV cabinet |  |  |  |  |
|  | - width / length / height |  | mm | Specify |  |
|  | 13. Maintenance |  |  |  |  |
|  | • Small inspection intervals (detailled activities) |  | Year | Specify |  |
|  | • Important maintenance intervals (detailled activities) |  | Year | Specify |  |
|  | • Minimum operation before maintenance |  |  | Specify |  |
|  | • Other |  |  | Specify |  |
|  | 14. Paint and corrosion protection |  |  |  |  |
|  | • Finishing colour |  |  | Specify |  |
|  | • Anticorrosion protection |  |  | Yes |  |
|  | - Treatment of the enclosures |  |  | Specify |  |
|  | - Treatment of the steel structures |  |  | Specify |  |
|  | - Non corrosion durability |  | Year | Specify |  |
|  | - Bolts, nuts, …are |  |  |  |  |
|  | . in stainless steel for diameters < M16 |  |  | Yes |  |
|  | . for diameters > M16: hot dip galvanised and painted. |  |  | Yes |  |
|  | - Special protection |  |  | N.A. |  |
|  | - Metal parts: hot dip galvanised |  |  | Yes |  |
|  | • Earthing connections, metal conductors, … will be free of paint |  |  | Yes |  |
|  | 15. Testing |  |  |  |  |
|  | • Routine (Acc. to IEC) |  |  | Yes |  |
|  | • On factory and on site tests |  |  | Yes |  |
|  | 16. Documents to be supplied |  |  |  |  |
|  | • At offer |  |  | 3 ex. |  |
|  | - Technical schedules duly complited |  |  |  |  |
|  | - Outline drawing, with dimensions, weights and efforts |  |  |  |  |
|  | - Standards test reports for the offered equipment |  |  |  |  |
|  | - Certificates for type and special test, done on similar material |  |  |  |  |
|  | - Description catalogues, brochure and documents |  |  |  |  |
|  | - Preliminary diagrams of principle |  |  |  |  |
|  | - Operating, assembly and maintenance instructions |  |  |  |  |
|  | - Price list for spare parts |  |  |  |  |
|  | - Earthing procedure for intrusive interventions |  |  |  |  |
|  | - Description of the special testing device |  |  |  |  |
|  | - Procedure for M.V. cable testing |  |  |  |  |
|  | - Description of pressure relief device on each compartment |  |  |  |  |
|  | - Paint procedure |  |  |  |  |
|  | - Necessary information about transport |  |  |  |  |
|  | • At order |  |  | 3 ex. |  |
|  | - Instructions for operation, inspection and maintenance |  |  |  |  |
|  | - A manual describing the different operations and locking |  |  |  |  |
|  | - Necessary safety and security documents |  |  |  |  |
|  | - Safety instructions for maintenance and repair |  |  |  |  |
|  | - Transport plan |  |  |  |  |
|  | - Plan of rating plates |  |  |  |  |
|  | - Construction file (user manual; maintenance and installation manuals; plans, As built plans, diagrams and drawings; routine, factory acceptance and site test reports, end of assembly reports,…) |  |  |  |  |
|  | • Completed Manufactuer final report including |  |  | 3 ex. |  |
|  | - instruction manual |  |  |  |  |
|  | - erection instruction manual |  |  |  |  |
|  | - maintenance instruction manual |  |  |  |  |
|  | - as built drawings and diagrams |  |  |  |  |
|  | - Detailed layout drawing |  |  |  |  |
|  | - drawing of the LV cabinets |  |  |  |  |
|  | - Drawing of the rating plate |  |  |  |  |
|  | - Detailed description of accessories |  |  |  |  |
|  | - Standard routine, factory, on site test reports |  |  |  |  |
|  | 17. Languages |  |  |  |  |
|  | • All documents establish in English |  |  | Yes |  |

| TECHNICAL SCHEDULE – Main Data |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Combinated Disconnector and Earthing - 10kV |  |  |  |  |  |
| Description |  |  | Units | Imposed Values | Guaranteed Values* |
|  | 1. General characteristics |  |  |  |  |
|  | • Manufacturer |  |  | Specify |  |
|  | • Type |  |  | Specify |  |
|  | • Number of poles |  |  | 3 |  |
|  | • Single break disconnector |  |  | Yes |  |
|  | • Earthing switch on line side |  |  | Yes |  |
|  | • Earthing switch on CB side |  |  | Yes |  |
|  | • Indoor/Outdoor installation |  |  | Outdoor |  |
|  | • Maximum opening time |  | s | 10 |  |
|  | • Maximum closing time |  | s | 10 |  |
|  | • Number of switching events until the first maintenance |  |  | 1000 |  |
|  | • Insulator type |  |  | Brown Porcelain |  |
|  | • Minimum nominal creeping distance |  | mm / kV | 31 |  |
|  | 2. Currents Characteristics |  |  |  |  |
|  | • Rated current |  | A | 2500 |  |
|  | • Rated short time withstand current |  | kA | 25 |  |
|  | • Rated peak withstand current |  | kA peak | 65 |  |
|  | • Rated duration of short circuit |  | s | 3 |  |
|  | 3. Rated voltage and rated insulation level |  |  |  |  |
|  | • Service voltage |  | kV | 10 |  |
|  | • Rated voltage (Ur) |  | kV | 12 |  |
|  | • Rated frequency |  | Hz | 50 |  |
|  | • Rated duration short-duration power-frequency withstand voltage (Ud) |  |  |  |  |
|  | - Phase to earth |  | kV | 28 |  |
|  | - Across open switching device |  | kV | 32 |  |
|  | • Rated lightning impulse withstand voltage (1,2/50µs) (Up) |  |  |  |  |
|  | - Phase to earth |  | kV peak | 75 |  |
|  | - Across open switching device |  | kV peak | 85 |  |
|  | • Minimum nominal creeping distance |  | mm / kV | 31 |  |
|  | • Height |  | mm | Specify |  |
|  | • Weight |  | kg | Specify |  |
|  | 4. Disconnector operating device |  |  |  |  |
|  | Main blades |  |  |  |  |
|  | • Type of operating device |  |  |  |  |
|  | • Three or single pole operated |  |  | three pole |  |
|  | • Motorized or manual operated |  |  | manual |  |
|  | • Number of potential free auxiliary contacts |  |  |  |  |
|  | - Closed – Open - Open: COO |  |  | 4 |  |
|  | - Open – Open - Closed: OOC |  |  | 4 |  |
|  | • Heating |  |  |  |  |
|  | - Rated voltage |  | Vca | 230 |  |
|  | Earth blades for Breaker Maintenance and Busbar |  |  |  |  |
|  | • Type of operating device |  |  |  |  |
|  | • Three or single pole operated |  |  | three pole |  |
|  | • Motorized or manual operated |  |  | manual |  |
|  | • Number of potential free auxiliary contacts |  |  |  |  |
|  | - Closed – Open - Open: COO |  |  | 4 |  |
|  | - Open – Open - Closed: OOC |  |  | 4 |  |
|  | • Heating |  |  |  |  |
|  | - Rated voltage |  | Vca | 230 |  |

| TECHNICAL SCHEDULE – Data for Information |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Combinated Disconnector and Earthing - 10kV |  |  |  |  |  |
| Description |  |  | Units | Imposed Values | Guaranteed Values* |
|  | 1. General characteristics |  |  |  |  |
|  | • Place of manufacture |  |  | Specify |  |
|  | • Standards (latest edition) |  |  | IEC 62271-102 |  |
|  | • Class |  |  |  |  |
|  | - Main blades |  |  | M1 |  |
|  | - Earth blades |  |  | E1 |  |
|  | 2. Normal service conditions(please refer to the site conditions of each substation) |  |  |  |  |
|  | • Ambient temperature range |  | °C |  |  |
|  | • Relative humidity |  | % |  |  |
|  | • Maximum altitude |  | m |  |  |
|  | • Maximum ice coating |  | mm |  |  |
|  | • Maximum pressure of the wind speed |  | Pa |  |  |
|  | • Solar radiation |  | W/m² |  |  |
|  | 3. Currents Characteristics |  |  |  |  |
|  | • Maximum temperature rise at In (t° ambient: 45°C) |  |  | Specify |  |
|  | 4. Rated voltage and rated insulation level |  |  |  |  |
|  | • Contact resistance |  |  |  |  |
|  | - Main blades |  | μΩ | Specify |  |
|  | - Earth blades |  | μΩ | Specify |  |
|  | 5. Overload conditions |  |  |  |  |
|  | • Permissible overload currents in accordance with the standard IEC 62271-1 |  |  | Yes |  |
|  | 6. Insulators characteritics |  |  |  |  |
|  | • Manufacturer |  |  | Specify |  |
|  | • Type (based IEC) |  |  | Specify |  |
|  | • Used material |  |  | Ceramic |  |
|  | • Profile |  |  | Specify |  |
|  | • Number of elements |  |  | 1 |  |
|  | • Height |  | mm | Specify |  |
|  | • Weight |  | kg | Specify |  |
|  | 7. Disconnector operating device |  |  |  |  |
|  | Main blades |  |  |  |  |
|  | • Type (manufacturer reference) |  |  | Specify |  |
|  | - Maximal torque needed for manual opening |  | Nm | Specify |  |
|  | - Maximal torque needed for manual closing |  | Nm | Specify |  |
|  | - Maximal operation height above ground level |  | mm | 1500 |  |
|  | • Number of potential free auxiliary contacts |  |  |  |  |
|  | - Breaking capacity |  |  | 4 A at 220 V |  |
|  | - Minimum rated current |  |  | 10 A (class 1) |  |
|  | • Heating |  |  |  |  |
|  | - Rated voltage |  | Vca | 230 |  |
|  | - Tolerance |  | % | 85 - 110 |  |
|  | - Power |  | W | Specify |  |
|  | • Protection level |  |  | ≥IP 55 |  |
|  | Earth blades for Breaker Maintenance and Busbar |  |  |  |  |
|  | • Type (manufacturer reference) |  |  | Specify |  |
|  | - Maximal torque needed for manual opening |  | Nm | Specify |  |
|  | - Maximal torque needed for manual closing |  | Nm | Specify |  |
|  | - Maximal operation height above ground level |  | mm | 1500 |  |
|  | • Number of potential free auxiliary contacts |  |  |  |  |
|  | - Breaking capacity |  |  | 4 A at 220 V |  |
|  | - Minimum rated current |  |  | 10 A (class 1) |  |
|  | • Heating |  |  |  |  |
|  | - Rated voltage |  | Vca | 230 |  |
|  | - Tolerance |  | % | 85 - 110 |  |
|  | - Power |  | W | Specify |  |
|  | • Protection level |  |  | ≥IP 55 |  |
|  | 8. Safety and locking |  |  |  |  |
|  | Main blades |  |  |  |  |
|  | • Normal electrical operated mechanism |  |  |  |  |
|  | - Mechanical locking device placed on motor drive |  |  | Yes |  |
|  | - Motor circuit interrupted by the locking device |  |  | Yes |  |
|  | - Padlockable mechanical locking device in open and closed position (padlocking Ø8mm possible) |  |  | Yes |  |
|  | • Manual drive (if applicable) |  |  | N.A. |  |
|  | - Locking coil in combination with push button |  |  | N.A. |  |
|  | - Supply voltage |  | Vdc | N.A. |  |
|  | - Padlockable mechanical locking device in open and closed position (padlocking Ø8mm possible) |  |  | N.A. |  |
|  | Earth blades for lines |  |  |  |  |
|  | • Normal electrical operated mechanism |  |  |  |  |
|  | - Mechanical locking device placed on motor drive |  |  | Yes |  |
|  | - Motor circuit interrupted by the locking device |  |  | Yes |  |
|  | - Padlockable mechanical locking device in open and closed position (padlocking Ø8mm possible) |  |  | Yes |  |
|  | • Manual drive (if applicable) |  |  | N.A. |  |
|  | - Locking coil in combination with push button |  |  | N.A. |  |
|  | - Supply voltage |  | Vdc | N.A. |  |
|  | - Padlockable mechanical locking device in open and closed position (padlocking Ø8mm possible) |  |  | N.A. |  |
|  | Earth blades for Breaker maintenance and Busbar |  |  |  |  |
|  | - Locking coil in combination with push button |  |  | Yes |  |
|  | - Supply voltage |  | Vdc | 220 |  |
|  | - Padlockable mechanical locking device in open and closed position (padlocking Ø8mm possible) |  |  | Yes |  |
|  | Main blades and Earth blades |  |  |  |  |
|  | - Mechanical interlock between main and earth blades |  |  |  |  |
|  | 9. Ergonomics |  |  |  |  |
|  | • Minimum height from ground or circulation level |  |  |  |  |
|  | - bottom skirt of the isolator |  | mm | 2500 |  |
|  | - vertical distance of life part |  | mm | 4500 |  |
|  | • Preferential height from ground or circulation level |  |  |  |  |
|  | - bottom side of the drives |  | mm | 1000 < H < 1600 |  |
|  | - top side of the drives |  | mm | Maximum 2500 |  |
|  | - door handles |  | mm | Maximum 1800 |  |
|  | 10. Mechanical characteristics |  |  |  |  |
|  | • Weight of the complete disconnector |  | kg | Specify |  |
|  | • Weight of the operating mechanisms |  |  |  |  |
|  | - Weight of the main blades operating mechanism |  | kg | Specify |  |
|  | - Weight of the earth blades operating mechanism |  | kg | Specify |  |
|  | 11. Construction details |  |  |  |  |
|  | Main blades |  |  |  |  |
|  | - Used material for contact (Al, electroplated silver or tinned copper) |  |  | Specify |  |
|  | - Contact type |  |  | Specify |  |
|  | - Maximum temperature rise at In (t° ambient: 45°C) |  |  | Specify |  |
|  | - Number of contact fingers |  |  | Specify |  |
|  | - Contact pressure by finger |  | daN | Specify |  |
|  | - Type of electrical connection between elements |  |  | Specify |  |
|  | • HV Terminals |  |  |  |  |
|  | - Diameter (according Inom) |  |  | Specify |  |
|  | - Used material for contact (Al, electroplated silver or tinned copper) |  |  | Specify |  |
|  | - Length |  |  | Specify |  |
|  | - Supply all the parts needed for connecting connection |  |  | Yes |  |
|  | Earth blades |  |  |  |  |
|  | - Used material for contact (Al, electroplated silver or tinned copper) |  |  | Specify |  |
|  | - Contact type |  |  | Specify |  |
|  | - Number of contact fingers |  |  | Specify |  |
|  | - Contact pressure by finger |  | daN | Specify |  |
|  | 12. Paint and corrosion protection |  |  |  |  |
|  | • Oxydable metal parts |  |  | hot dip galvanizing |  |
|  | • Screws, nuts, bolts,…. |  |  |  |  |
|  | - for diameter ≤ M16 stainless steel |  |  | Yes |  |
|  | - for diameter > M16 hot dip galvanized steel and painted |  |  | Yes |  |
|  | • Frame of control panel galvanized |  |  | Yes |  |
|  | • Duplex principle (galvanized + paint) according GTS |  |  | Yes |  |
|  | • Final color paint |  |  |  |  |
|  | - pieces to earth |  |  | Specify |  |
|  | - live parts |  |  | Specify |  |
|  | - insulator's metal flanges |  |  | Specify |  |
|  | - grounded connections, metallic conductors,… free of paint |  |  |  |  |
|  |  |  |  |  |  |
|  | 13. Documents to be submitted |  |  |  |  |
|  | • Submital fase |  |  | 3 ex. |  |
|  | - General documentation |  |  |  |  |
|  | - List of references |  |  |  |  |
|  | - Type test reports |  |  |  |  |
|  | - datasheet completed |  |  |  |  |
|  | - dimensional drawing |  |  |  |  |
|  | • Ordering fase |  |  | 3 ex. |  |
|  | - operating instruction manual |  |  |  |  |
|  | - erection instruction manual |  |  |  |  |
|  | - maintenance instruction manual |  |  |  |  |
|  | - static and dynamic efforts |  |  |  |  |
|  | - drawings |  |  |  |  |
|  | - detailed dimensional drawing with an indication of weight and efforts |  |  |  |  |
|  | - drawing of the operating cubicles |  |  |  |  |
|  | - drawing of the rating plate |  |  |  |  |
|  | - LV diagrams |  |  |  |  |
|  | - drawing of electrical circuits |  |  |  |  |
|  | - principle diagram of the operating mechanism for main blades |  |  |  |  |
|  | - principle diagram of the operating mechanism for earth blades |  |  |  |  |
|  | • Completed Manufactuer final report including |  |  | 3 ex. |  |
|  | - operating instruction manual |  |  |  |  |
|  | - erection instruction manual |  |  |  |  |
|  | - maintenance instruction manual |  |  |  |  |
|  | - as built drawings and schematics |  |  |  |  |
|  | - factory test report |  |  |  |  |
|  | 14. Languages |  |  |  |  |
|  | • All documents establish in English |  |  | Yes |  |

| TECHNICAL SCHEDULE – Main Data |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Insulating support - 10kV |  |  |  |  |  |
| Description |  |  | Units | Imposed Values | Guaranteed Values |
|  | 1. General characteristics |  |  |  |  |
|  | • Manufacturer |  |  | Specify |  |
|  | • Type |  |  | Specify |  |
|  | • Installation |  |  | Outdoor |  |
|  | • Housing (porcelain, polymer) |  |  | Brown Porcelain |  |
|  | • Minimum phase creepage distance |  | mm/kV | 31 |  |
|  | 2. Electrical characteristics |  |  |  |  |
|  | • Rated frequency (fr) |  | Hz | 50 |  |
|  | • Network nominal voltage |  | kV | 10 |  |
|  | • Maximum service voltage (Um) |  | kV | 12 |  |
|  | - Power frequency withstand voltage 50Hz - 1 min.(Ud) |  | kV | 28 |  |
|  | - Lightning Impulse withstand voltage (1,2/50µs) |  | kV | 75 |  |

| TECHNICAL SCHEDULE – Data for Information |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Insulating support - 10kV |  |  |  |  |  |
| Description |  |  | Units | Imposed Values | Guaranteed Values |
|  | 1. General characteristics |  |  |  |  |
|  | •Place of manufacture |  |  | Specify |  |
|  | • Standards |  |  | IEC 60273 |  |
|  | 2. Normal service conditions(please refer to the site conditions of each substation) |  |  |  |  |
|  | • Ambient temperature range |  | °C |  |  |
|  | • Relative humidity |  | % |  |  |
|  | • Maximum altitude |  | m |  |  |
|  | • Maximum ice coating |  | mm |  |  |
|  | • Maximum pressure of the wind speed |  | Pa |  |  |
|  | • Solar radiation |  | W/m² |  |  |
|  | 3. Mechanical characteristics |  |  |  |  |
|  | • Flexion |  |  |  |  |
|  | -breaking load |  | N | Specify |  |
|  | -permissible continuous effort on top without damage |  | % | Specify |  |
|  | -permissible effort on top on short circuit without damage |  | % | Specify |  |
|  | -duration |  | s | Specify |  |
|  | • Torsion: breaking load |  | Nm | Specify |  |
|  | • Strength: breaking load |  | N | Specify |  |
|  | • Compression: breaking load |  | N | Specify |  |
|  | 4. Characteristics of insulating support |  |  |  |  |
|  | • Mounting |  |  | standing or hanging |  |
|  | • Number of elementary columns |  |  | Specify |  |
|  | • Total height of the insulating support |  | mm | Specify |  |
|  | • Fixations |  |  |  |  |
|  | -top (voltage side) |  |  |  |  |
|  | -circle diameter of fixation |  | mm | Specify |  |
|  | -number of screws |  |  | Specify |  |
|  | -drillings for screws |  |  | Specify |  |
|  | -base (earth side) |  |  |  |  |
|  | -circle diameter of fixation |  | mm | Specify |  |
|  | -number of screws |  |  | Specify |  |
|  | -drillings for screws |  |  | Specify |  |
|  | • Weight |  | kg | Specify |  |
|  | 5. Paint and corrosion protection |  |  |  |  |
|  | • Oxydable metal parts |  |  | hot dip galvanizing |  |
|  | • Screws, nuts, bolts,…. |  |  |  |  |
|  | - for diameter ≤ M16 stainless steel |  |  | Yes |  |
|  | - for diameter > M16 hot dip galvanized steel and painted |  |  | Yes |  |
|  | • Duplex principle (galvanized + paint) according GTS |  |  | Yes |  |
|  | • Final color paint |  |  |  |  |
|  | - pieces to earth |  |  | Specify |  |
|  | - live parts |  |  | Specify |  |
|  | - insulator's metal flanges |  |  | Specify |  |
|  | - grounded connections, metallic conductors,… free of paint |  |  |  |  |
|  |  |  |  |  |  |
|  | 6. Documents to be submitted |  |  |  |  |
|  | • Submital fase |  |  | 3 ex. |  |
|  | - General documentation |  |  |  |  |
|  | - datasheet completed |  |  |  |  |
|  | - dimensional drawing |  |  |  |  |
|  | • Ordering fase |  |  | 3 ex. |  |
|  | - erection instruction manual |  |  |  |  |
|  | - maintenance instruction manual |  |  |  |  |
|  | - static and dynamic efforts |  |  |  |  |
|  | - dimensional drawing |  |  |  |  |
|  | • Completed Manufactuer final report including |  |  | 3 ex. |  |
|  | - erection instruction manual |  |  |  |  |
|  | - maintenance instruction manual |  |  |  |  |
|  | - as built drawing |  |  |  |  |
|  | 7. Languages |  |  |  |  |
|  | • All documents establish in English |  |  | Yes |  |

| TECHNICAL SCHEDULE – Main Data |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Phase Surge Arrester - 10kV |  |  |  |  |  |
| Description |  |  | Units | Imposed Values | Guaranteed Values |
|  | 1. General characteristics |  |  |  |  |
|  | • Manufacturer |  |  | Specify |  |
|  | • Type |  |  | Specify |  |
|  | • Installation |  |  | Outdoor |  |
|  | • Housing (porcelain, polymer) |  |  | Brown Porcelain |  |
|  | • Minimum phase creepage distance |  | mm/kV | 31 |  |
|  | 2. Electrical characteristics |  |  |  |  |
|  | • Rated frequency (fr) |  | Hz | 50 |  |
|  | • Network nominal voltage |  | kV | 10 |  |
|  | • Maximum service voltage (Um) |  | kV | 12 |  |
|  | • Nominal discharge current |  | kA peak | 10 |  |
|  | • Continuous Operating Voltage (Uc - COV) |  | kV | 7 |  |
|  | • Insulation level for the housing |  |  |  |  |
|  | - Power frequency withstand voltage 50Hz - 1 min. for the housing |  | kV | 28 |  |
|  | - Lightning Impulse withstand voltage (1,2/50µs) for the housing |  | kV | 75 |  |

| TECHNICAL SCHEDULE – Data for Information |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Phase Surge Arrester - 10kV |  |  |  |  |  |
| Description |  |  | Units | Imposed Values | Guaranteed Values |
|  | 1. General characteristics |  |  |  |  |
|  | •Place of manufacture |  |  | Specify |  |
|  | • Standards |  |  | IEC |  |
|  | • Construction type |  |  | MO (metal oxide) |  |
|  | • Model |  |  | Specify |  |
|  | • Surge counter |  |  | Yes |  |
|  | -number |  |  | 1 by phase |  |
|  | -type |  |  | Specify |  |
|  | 2. Normal service conditions(please refer to the site conditions of each substation) |  |  |  |  |
|  | • Ambient temperature range |  | °C |  |  |
|  | • Relative humidity |  | % |  |  |
|  | • Maximum altitude |  | m |  |  |
|  | • Maximum ice coating |  | mm |  |  |
|  | • Maximum pressure of the wind speed |  | Pa |  |  |
|  | • Solar radiation |  | W/m² |  |  |
|  | 3. Electrical characteristics |  |  |  |  |
|  | • Surge arrester rated voltage (Ur) |  | kV | Specify |  |
|  | • Maximum temporary Over Voltage |  |  |  |  |
|  | - for 1 s |  | kV | Specify |  |
|  | - for 10 s |  | kV | Specify |  |
|  | • Maximum residual voltages for a lightning impulse 8/20 μs |  |  |  |  |
|  | - at I = 5 kA |  | kV peak | Specify |  |
|  | - at I = 10 kA |  | kV peak | Specify |  |
|  | - at I = 20 kA |  | kV peak | Specify |  |
|  | • Maximum residual voltages for a lightning impulse 30/... μs |  |  |  |  |
|  | - at I = 1 kA |  | kV peak | Specify |  |
|  | • Line discharge class (IEC 60099-4) |  |  | Specify |  |
|  | • Reference current and voltage |  | kV /mA | Specify |  |
|  | 4. Mechanical characteristics |  |  |  |  |
|  | • Pollution Class |  |  | outstanding (no pollution) |  |
|  | • Over-pressure valve |  |  | Yes/No |  |
|  | - type |  |  | Specify |  |
|  | - pressure relief capability |  | kA | ≥25 |  |
|  | • Maximum allowed strength (MPSL) |  | N | Specify |  |
|  | • Maximum dynamic allowed strength (MPDSL) |  | N | Specify |  |
|  | • Total height (including insulated base) |  | mm | Specify |  |
|  | • Total weight |  | kg | Specify |  |
|  | 5. Contruction details |  |  |  |  |
|  | • Type of line connection (Al, ...) |  |  | Specify |  |
|  | • Type of ground connection ( stainless steel, ….) |  |  | Specify |  |
|  | • Insulated base |  |  | Yes |  |
|  | • Guard ring (outer diameter) |  | mm | Specify |  |
|  | • Number of elementary columns |  |  | Specify |  |
|  | • Terminal for connection of online Leakage Current Measurement system |  |  | Yes |  |
|  | 6. Paint and corrosion protection |  |  |  |  |
|  | • Oxydable metal parts |  |  | hot dip galvanizing |  |
|  | • Screws, nuts, bolts,…. |  |  |  |  |
|  | - for diameter ≤ M16 stainless steel |  |  | Yes |  |
|  | - for diameter > M16 hot dip galvanized steel and painted |  |  | Yes |  |
|  | • Duplex principle (galvanized + paint) according GTS |  |  | Yes |  |
|  | • Final color paint |  |  |  |  |
|  | - pieces to earth |  |  | Specify |  |
|  | - live parts |  |  | Specify |  |
|  |  |  |  |  |  |
|  | 7. Testing |  |  |  |  |
|  | • Reports of type tests on similar equipment |  |  | Yes |  |
|  | • Routine test according to IEC 60099.4 |  |  | Yes |  |
|  | 8. Documents to be submitted |  |  |  |  |
|  | • Submital fase |  |  | 3 ex. |  |
|  | - General documentation |  |  |  |  |
|  | - List of references |  |  |  |  |
|  | - Type test reports |  |  |  |  |
|  | - datasheet completed |  |  |  |  |
|  | - dimensional drawing |  |  |  |  |
|  | • Ordering fase |  |  | 3 ex. |  |
|  | - erection instruction manual |  |  |  |  |
|  | - maintenance instruction manual |  |  |  |  |
|  | - static and dynamic efforts |  |  |  |  |
|  | - voltage curve at power-frequency in function of time |  |  |  |  |
|  | - drawings |  |  |  |  |
|  | - detailed dimensional drawing |  |  |  |  |
|  | - drawing of the rating plate |  |  |  |  |
|  | • Completed Manufactuer final report including |  |  | 3 ex. |  |
|  | - erection instruction manual |  |  |  |  |
|  | - maintenance instruction manual |  |  |  |  |
|  | - as built drawings |  |  |  |  |
|  | - voltage curve at power-frequency in function of time |  |  |  |  |
|  | - factory test report |  |  |  |  |
|  | 8. Languages |  |  |  |  |
|  | • All documents establish in English |  |  | Yes |  |

| TECHNICAL SCHEDULE – Main Data Air Insultated Switchgear AIS - 10 kV |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Description |  |  | Units | Imposed Values | Guaranteed Values |
|  | 1. General characteristics |  |  |  |  |
|  | • Manufacturer |  |  | Specify |  |
|  | • AIR Insulated metal-enclosed Switchgear (AIS) |  |  | Yes |  |
|  | • Indoor use |  |  | Yes |  |
|  | • Withdrawable Components |  |  | Yes |  |
|  | • Rated Maximum voltage (Ur) |  | kV | 12 |  |
|  | • Rated frequency (fr) |  | Hz | 50 |  |
|  | • Busbar system: Single, double |  |  | Single |  |
|  | • Method of earthing – Busbars side |  |  | Specify |  |
|  | • Method of earthing - Line side |  |  | Specify |  |
|  | • Busbars Segregated |  |  | Yes |  |
|  | • Material of cover and Portions |  |  | Metallic |  |
|  | • Material of Shutters |  |  | Metallic/earth |  |
|  | • Busbars and joints fully encapsulated |  |  | Yes |  |
|  | • Emergency manual trip facility (during failure of DC supply) |  |  | Yes |  |
|  | • Porcelain Color |  |  | Brown |  |
|  | 2. Rated Currents |  |  |  |  |
|  | • Rated currents |  |  |  |  |
|  | - Busbars |  | A | 2500 |  |
|  | - Incoming panel (transformer) |  | A | 2500 |  |
|  | - Busbar coupler |  | A | 2500 |  |
|  | - Outgoing panel (feeders) |  | A | 630 |  |
|  | • Rated short time withstand current (Ik) |  | kA | 25 |  |
|  | • Rated duration of short circuit (tk) |  | s | 3 |  |
|  | • Rated peak withstand current (Ip) |  | kA peak | 80 |  |
|  | 3. Rated voltage and rated insulation level |  |  |  |  |
|  | • Service voltage |  | kV | 10 |  |
|  | • Rated short duration power-frequency withstand voltage (AC) 1min-50Hz (Ud) – Phase to earth |  | kV | 28 |  |
|  | • Rated short duration power-frequency withstand voltage (AC) 1min-50Hz (Ud) – Across the isolating distance |  | kV | 32 |  |
|  | • Rated lightning impulse withstand voltage (1,2/50µs) (Up) – Phase to earth |  | kV | 75 |  |
|  | • Rated lightning impulse withstand voltage (1,2/50µs) (Up) – Across the isolating distance |  | kV | 85 |  |
|  | 4. Main Busbars |  |  |  |  |
|  | • material |  |  | Copper |  |
|  | • surface treatment (painted, insulated,….) |  |  | Silver plated copper |  |
|  | • Rated current at 50°C (corresponding to site rating) |  | A | 2500 |  |
|  | 5. Circuit Breaker |  |  |  |  |
|  | • Manufacturer |  |  | Specify |  |
|  | • Quenching fluid |  |  | Vacuum |  |
|  | • Withdrawable |  |  | Yes |  |
|  | • Fully encapsulated |  |  | Yes |  |
|  | • Rated maximum voltage (Ur) |  | kV | 12.5 |  |
|  | • Rated frequency (fr) |  | Hz | 50 |  |
|  | • Rated short duration power-frequency withstand voltage (AC) 1min-50Hz (Ud) – Phase to earth |  | kV | 28 |  |
|  | • Rated short duration power-frequency withstand voltage (AC) 1min-50Hz (Ud) – Across the isolating distance |  | kV | 32 |  |
|  | • Rated lightning impulse withstand voltage (1,2/50µs) (Up) – Phase to earth |  | kV | 75 |  |
|  | • Rated lightning impulse withstand voltage (1,2/50µs) (Up) – Across the isolating distance |  | kV | 85 |  |
|  | • Rated short circuit breaking current |  | kA | 25 |  |
|  | • Rated peak withstand current (Ip) |  | kA peak | 63 |  |
|  | • First-pole-to-clear-factor |  |  | 1.5 |  |
|  | • Rated Current |  |  |  |  |
|  | - Incoming panel (transformer) |  | A | 2500 |  |
|  | - Busbar Coupler |  | A | 2500 |  |
|  | - Outgoing panel (feeders) |  | A | 630 |  |
|  | • Operating sequence O-0,3s-CO-3min-CO |  |  | Yes |  |
|  | • Type of operating mechanism |  |  | 3 pole |  |
|  | • Manual spring discharge facility |  |  | Yes |  |
|  | • Type of power device |  |  | Motor – Spring |  |
|  | • Nominal control and operating voltage |  | V DC | 220 |  |
|  | • Nominal heater voltage |  | V AC | 220 |  |
|  | 6. Busbars disconnector or busbars switch |  |  |  |  |
|  | • Manufacturer |  |  | Specify |  |
|  | • Type |  |  | Specify |  |
|  | • Rated voltage (Ur) |  | kV | 12 |  |
|  | • Rated frequency (fr) |  | Hz | 50 |  |
|  | • Rated short duration power-frequency withstand voltage (AC) 1min-50Hz (Ud) – Phase to earth |  | kV | 28 |  |
|  | • Rated lightning impulse withstand voltage (1,2/50µs) (Up) – Phase to earth |  | kV | 75 |  |
|  | • Rated Current |  |  |  |  |
|  | - Busbar Coupler |  | A | 2500 |  |
|  | • Type of contact |  |  | Copper |  |
|  | 7. Making proof Earthing switch |  |  |  |  |
|  | • Manufacturer |  |  | Specify |  |
|  | • Type |  |  | Specify |  |
|  | • Rated voltage (Ur) |  | kV | 12 |  |
|  | • Rated frequency (fr) |  | Hz | 50 |  |
|  | • Rated short duration power-frequency withstand voltage (AC) 1min-50Hz (Ud) – Phase to earth |  | kV | 28 |  |
|  | • Rated lightning impulse withstand voltage (1,2/50µs) (Up) – Phase to earth |  | kV | 75 |  |
|  | • Rated short time withstand current (Ik) |  | kA | 25 |  |
|  | • Rated duration of short circuit (tk) |  | s | 3 |  |
|  | • Type of contact |  |  | Copper |  |
|  | 8. Current transformer |  |  |  |  |
|  | • Manufacturer |  |  | Specify |  |
|  | • Type |  |  | Cast Resin multicore, multi ratio, indoor |  |
|  | • Rated voltage (Ur) |  | kV | 12 |  |
|  | • Rated short duration power-frequency withstand voltage (AC) 1min-50Hz (Ud) – Phase to earth |  | kV | 28 |  |
|  | • Rated lightning impulse withstand voltage (1,2/50µs) (Up) – Phase to earth |  | kV | 75 |  |
|  | • Incoming Feeder |  |  |  |  |
|  | - Secondary Current |  | A | 1/1/5 |  |
|  | - Primary Current incoming / bus coupler |  | A | 1250-2500 |  |
|  | - Number of measuring cores |  |  | 1 |  |
|  | - Number of protection cores |  |  | 2 |  |
|  | • Outgoing Feeder |  |  |  |  |
|  | - Secondary Current |  | A | 1/5 |  |
|  | - Primary Current outgoing |  | A | 100-300-600 |  |
|  | - Number of measuring cores |  |  | 1 |  |
|  | - Number of protection cores |  |  | 1 |  |
|  | • For Earth-Fault relays |  |  |  |  |
|  | - Secondary Current |  | A | 1 |  |
|  | - Primary Current outgoing |  | A | 50 |  |
|  | - Number of protection cores |  |  | 1 |  |
|  | • Accuracy class rating and capacity of measuring core |  |  | 0.5/10 |  |
|  | • Accuracy class rating and capacity of protection core |  |  | 10P20 |  |
|  | 9. Voltage transformer |  |  |  |  |
|  | • Manufacturer |  |  | Specify |  |
|  | • Type |  |  | Inductive cast resin single pole insulated |  |
|  | • Rated voltage (Ur) |  | kV | 12 |  |
|  | • Rated frequency (fr) |  | Hz | 50 |  |
|  | • Rated short duration power-frequency withstand voltage (AC) 1min-50Hz (Ud) – Phase to earth |  | kV | 28 |  |
|  | • Rated lightning impulse withstand voltage (1,2/50µs) (Up) – Phase to earth |  | kV | 75 |  |
|  | • Transformation Factor |  |  | 10000/√3 - 100/√3 - 100/√3 |  |
|  | • Accuracy class rating and capacity of measuring core and protection |  |  | 0.5/30 VA |  |
|  | • Accuracy class protection |  |  | 3P / 30 VA |  |

| TECHNICAL SCHEDULE – Data for Information Air Insultated Switchgear AIS - 10 kV |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Description |  |  | Units | Imposed Values | Guaranteed Values |
|  | 1. General characteristics |  |  |  |  |
|  | • Place of manufacture |  |  | Specify |  |
|  | • Type |  |  | Specify |  |
|  | • Standards (last edition) |  |  | IEC 62271-200 |  |
|  | • Type of partitions (class PM or class PI) |  |  | PM |  |
|  | • Loss of service continuity classification |  |  | LSC2B |  |
|  | • Type of insulation |  |  | Air |  |
|  | • Internal Arc Classification (class IAC) |  |  | IAC-AFLR |  |
|  | • Expected life of the switchgear |  | Years | Specify |  |
|  | 2. Operating conditions(please refer to the site conditions of each substation) |  |  |  |  |
|  | • Ambient temperature range |  | °C |  |  |
|  | • Relative humidity |  | % |  |  |
|  | • Maximum altitude |  | m |  |  |
|  | • Maximum ice coating |  | mm |  |  |
|  | • Maximum pressure of the wind speed |  | Pa |  |  |
|  | • Solar radiation |  | W/m² |  |  |
|  | • Vibrations due to external causes |  |  |  |  |
|  | 3. Rated Currents |  |  |  |  |
|  | • Temperature rise according IEC |  |  | Yes |  |
|  | • Circuit Breaker breaking capacity at Un |  | kA | 25 |  |
|  | •Internal Arc withstand Current (IAC) |  | kA - 1s | 25 |  |
|  | • IAC classification |  |  | AFLR |  |
|  | 4. Technical characteristics of the auxiliary circuits |  |  |  |  |
|  | • Rated voltage |  |  |  |  |
|  | - operating circuits, signalization, tripping, locking and motors |  | Vdc | 220 |  |
|  | - operating range |  | % | 85 to 110 |  |
|  | • Auxiliary contacts |  |  |  |  |
|  | - rated continuous current (class 1) |  | A | 10 |  |
|  | - rated capacity |  | A | 4A/220Vdc |  |
|  | 5. Main Busbars |  |  |  |  |
|  | • section |  | mm² | Specify |  |
|  | 6. Circuit Breaker |  |  |  |  |
|  | • Type |  |  | Specify |  |
|  | • Type of operating mechanism |  |  | Specify |  |
|  | • Manufacturer reference |  |  |  |  |
|  | • Type (energy) |  |  | Spring |  |
|  | • Energy |  |  | Mechanical |  |
|  | • On/Off push button for emergency |  |  |  |  |
|  | - electrical |  |  | No |  |
|  | - mechanical |  |  | Yes |  |
|  | • Mechanical position indicator |  |  | Yes |  |
|  | - CB On/Off |  |  | Yes |  |
|  | - Spring charged/discharged |  |  | Yes |  |
|  | • Operations counter |  |  | Yes |  |
|  | • Emergency crank for spring bending |  |  | Yes |  |
|  | • LV circuit: |  |  |  |  |
|  | • Number of trip coils |  |  |  |  |
|  | -Incoming panel |  |  | 2 |  |
|  | -Coupling panel |  |  | 2 |  |
|  | -Feeder panel |  |  | 2 |  |
|  | • Number of closing coils |  |  |  |  |
|  | -Incoming panel |  |  | 2 |  |
|  | -Coupling panel |  |  | 2 |  |
|  | -Feeder panel |  |  | 2 |  |
|  | • Number of undervoltage coils |  |  | 0 |  |
|  | • Interlocking coil for withdrawable CB only incoming panel |  |  | Yes |  |
|  | • Antipumping |  |  | Yes |  |
|  | • Auxiliary position contacts |  |  |  |  |
|  | - CB On/Off |  |  | 4NO+4NC |  |
|  | - CB on withdrawable position |  |  | 2NO+2NC |  |
|  | - CB spring charged/discharged |  |  | 1NO+1NC |  |
|  | 7. Busbars disconnector or busbars switch |  |  |  |  |
|  | • Type |  |  | Specify |  |
|  | • Type of operating mechanism |  |  | Specify |  |
|  | • Auxiliary position contacts |  |  | 4NO+4NC |  |
|  | • Mechanical position indicator |  |  | Yes |  |
|  | • Interlocking coil with push button |  |  | Yes |  |
|  | 8. Making proof Earthing switch |  |  |  |  |
|  | • Type |  |  | Specify |  |
|  | • Closing capacity (type: "high speed"closure) |  | kA peak | 63 |  |
|  | • Type of operating mechanism |  |  | Manual |  |
|  | • Auxiliary position contacts |  |  | 4NO+4NC |  |
|  | • Mechanical position indicator on command side |  |  | Yes |  |
|  | • Interlocking coil with push button |  |  | Yes |  |
|  | • Busbars VT will be withdrawable |  |  | Yes |  |
|  | 9. Safety interlocking |  |  |  |  |
|  | • Interlocking |  |  | Specify |  |
|  | - CB + access to MV parts and earthing-switch |  |  | Specify |  |
|  | - Standard manufacturer's interlocking |  |  | Yes |  |
|  | - Others solution |  |  | Specify |  |
|  | - BB disconnector or BB switch |  |  | N.A. |  |
|  | • Voltage system detector |  |  | Yes |  |
|  | - according IEC 61243 part 5 |  |  | Yes |  |
|  | - On MV cables |  |  | Yes |  |
|  | • Mimic diagram showing all devices positions |  |  | Yes |  |
|  | • Padlockable operating devices (BB switch, BB disconnector, earthing-switch,…) |  |  | Yes |  |
|  | • Visible position of BB switch, BB disconnector, earthing-switch via windows |  |  | Yes |  |
|  | • Mechanical interlock of earthing-switch in open/close positions |  |  | Yes |  |
|  | • Labeling (panels, BB, phases,….) |  |  | following GTS |  |
|  | 10. Enclosures |  |  |  |  |
|  | • Three phase enclosure |  |  |  |  |
|  | - at busbar level |  |  | Yes |  |
|  | - at panel level |  |  | Yes |  |
|  | • Used material |  |  | Specify |  |
|  | • IP degree |  |  | ≥32 |  |
|  | • thickness of the partitions |  | mm | Specify |  |
|  | • closure of the bottom of the panels by non-magnetic cut sheets for MV cables entry |  |  | Yes |  |
|  | 11. Cable compartment |  |  |  |  |
|  | • Possible connections on: |  |  |  |  |
|  | - Incoming transformer feeders |  |  | Specify |  |
|  | - Outgoing feeders |  |  | Specify |  |
|  | • Maximum cable diameter |  |  | Specify |  |
|  | • Standard facilities for cable testing |  |  | Specify |  |
|  | • Minimum number of cables and section |  |  | showing on drawings |  |
|  | 12. Dimensions |  |  |  |  |
|  | As applicable: |  |  |  |  |
|  | • Incoming panel |  |  |  |  |
|  | - width / length / height |  | mm | Specify |  |
|  | - weight |  | Kg | Specify |  |
|  | • Outgoing panel |  |  |  |  |
|  | - width / length / height |  | mm | Specify |  |
|  | - weight |  | Kg | Specify |  |
|  | • Bus coupler panel |  |  |  |  |
|  | - width / length / height |  | mm | Specify |  |
|  | - weight |  | Kg | Specify |  |
|  | • Busbar VT |  |  |  |  |
|  | - width / length / height |  | mm | Specify |  |
|  | - weight |  | Kg | Specify |  |
|  | • Bus earthing |  |  |  |  |
|  | - width / length / height |  | mm | Specify |  |
|  | - weight |  | Kg | Specify |  |
|  | • AIS room |  |  |  |  |
|  | - minimum space at front of the switchgear |  | mm | Specify |  |
|  | - minimum space at rear of the switchgear |  | mm | Specify |  |
|  | - minimum space at top of the switchgear |  | mm | Specify |  |
|  | - minimum space at side of the switchgear |  | mm | Specify |  |
|  | - minimum needed space for extension of the switchgear |  | mm | Specify |  |
|  | - minimum height, the switchgear will be with an exhaust duct connected outside the building |  | mm | Specify |  |
|  | • Height of connecting of the cable terminals from the ground level |  | mm | Specify |  |
|  | • Ground fixations |  |  | Specify |  |
|  | • LV cabinet |  |  |  |  |
|  | - width / length / height |  | mm | Specify |  |
|  | 13. Maintenance |  |  |  |  |
|  | • Small inspection intervals (detailled activities) |  | Year | Specify |  |
|  | • Important maintenance intervals (detailled activities) |  | Year | Specify |  |
|  | • Minimum operation before maintenance |  |  | Specify |  |
|  | • Other |  |  | Specify |  |
|  | 14. Paint and corrosion protection |  |  |  |  |
|  | • Finishing colour |  |  | Specify |  |
|  | • Anticorrosion protection |  |  | Yes |  |
|  | - Treatment of the enclosures |  |  | Specify |  |
|  | - Treatment of the steel structures |  |  | Specify |  |
|  | - Non corrosion durability |  | Year | Specify |  |
|  | - Bolts, nuts, …are |  |  |  |  |
|  | . in stainless steel for diameters < M16 |  |  | Yes |  |
|  | . for diameters > M16: hot dip galvanised and painted. |  |  | Yes |  |
|  | - Special protection |  |  | N.A. |  |
|  | - Metal parts: hot dip galvanised |  |  | Yes |  |
|  | • Earthing connections, metal conductors, … will be free of paint |  |  | Yes |  |
|  | 15. Testing |  |  |  |  |
|  | • Routine (Acc. to IEC) |  |  | Yes |  |
|  | • On factory and on site tests |  |  | Yes |  |
|  | 16. Documents to be supplied |  |  |  |  |
|  | • At offer |  |  | 3 ex. |  |
|  | - Technical schedules duly complited |  |  |  |  |
|  | - Outline drawing, with dimensions, weights and efforts |  |  |  |  |
|  | - Standards test reports for the offered equipment |  |  |  |  |
|  | - Certificates for type and special test, done on similar material |  |  |  |  |
|  | - Description catalogues, brochure and documents |  |  |  |  |
|  | - Preliminary diagrams of principle |  |  |  |  |
|  | - Operating, assembly and maintenance instructions |  |  |  |  |
|  | - Price list for spare parts |  |  |  |  |
|  | - Earthing procedure for intrusive interventions |  |  |  |  |
|  | - Description of the special testing device |  |  |  |  |
|  | - Procedure for M.V. cable testing |  |  |  |  |
|  | - Description of pressure relief device on each compartment |  |  |  |  |
|  | - Paint procedure |  |  |  |  |
|  | - Necessary information about transport |  |  |  |  |
|  | • At order |  |  | 3 ex. |  |
|  | - Instructions for operation, inspection and maintenance |  |  |  |  |
|  | - A manual describing the different operations and locking |  |  |  |  |
|  | - Necessary safety and security documents |  |  |  |  |
|  | - Safety instructions for maintenance and repair |  |  |  |  |
|  | - Transport plan |  |  |  |  |
|  | - Plan of rating plates |  |  |  |  |
|  | - Construction file (user manual; maintenance and installation manuals; plans, As built plans, diagrams and drawings; routine, factory acceptance and site test reports, end of assembly reports,…) |  |  |  |  |
|  | • Completed Manufactuer final report including |  |  | 3 ex. |  |
|  | - instruction manual |  |  |  |  |
|  | - erection instruction manual |  |  |  |  |
|  | - maintenance instruction manual |  |  |  |  |
|  | - as built drawings and diagrams |  |  |  |  |
|  | - Detailed layout drawing |  |  |  |  |
|  | - drawing of the LV cabinets |  |  |  |  |
|  | - Drawing of the rating plate |  |  |  |  |
|  | - Detailed description of accessories |  |  |  |  |
|  | - Standard routine, factory, on site test reports |  |  |  |  |
|  | 17. Languages |  |  |  |  |
|  | • All documents establish in English |  |  | Yes |  |

| TECHNICAL SCHEDULE – Main Data Three phase Circuit Breaker – 110 kV – Three pole operated |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Description |  |  | Units | Imposed Values | Guaranteed Values* |
|  | 1. General characteristics |  |  |  |  |
|  | • Manufacturer |  |  | Specify |  |
|  | • Type |  |  | Specify |  |
|  | • Number of poles |  |  | 3 |  |
|  | • Indoor/Outdoor installation |  |  | Outdoor |  |
|  | • Quenching fluid |  |  | SF6 |  |
|  | • Network nominal voltage (Un) |  | kV | 110 |  |
|  | • Highest Operating Voltage (Um) |  | kV | 126 |  |
|  | • Rated frequency (fr) |  | Hz | 50 |  |
|  | • Number of breaking chamber per pole |  |  | 1 |  |
|  | • Action of CB operating mechanism |  |  | three pole |  |
|  | • Insulator |  |  | Brown Porcelain |  |
|  | • Minimum phase creepage distance |  | mm/kV | 31 |  |
|  | 2. Circuit breaker class |  |  |  |  |
|  | • minimum number of operations |  |  | 10 000 |  |
|  | • minimum number of operations at rated current before first maintenance |  |  | 3000 |  |
|  | • minimum number of operations at rated short-circuit current for each phase before first maintenance |  |  | 12 |  |
|  | • Percent of yearly gas leakage |  | % | ≤ 0,3 |  |
|  | 3. Normal service conditions |  |  |  |  |
|  | • Ambient temperature range |  | °C | -35 to +50 |  |
|  | 4. Rated withstand currents |  |  |  |  |
|  | • Rated bus transfer current |  | A | 1250 |  |
|  | • Rated line bay |  | A | 800 |  |
|  | • Rated autotransformer bay |  | A | 1250 |  |
|  | • Rated buscoupler bay |  | A | 2500 |  |
|  | • Rated short time withstand current |  | kA | 40 |  |
|  | • Rated peak withstand current |  | kA peak | 100 |  |
|  | • Rated duration of short circuit |  | s | 3 |  |
|  | 5. Rated voltage and rated insulation level |  |  |  |  |
|  | • Rated voltage for equipment (Ur) |  | kV | 123 |  |
|  | • Rated short duration power-frequency withstand voltage (AC) 1min-50Hz |  |  |  |  |
|  | - Between phases, phase to earth |  | kV | 230 |  |
|  | - Across open switching device |  | kV | 230 |  |
|  | • Rated lightning impulse withstand voltage (1,2/50µs) (Up) |  |  |  |  |
|  | - Between phases, phase to earth |  | kV peak | 550 |  |
|  | - Across open switching device |  | kV peak | 550 |  |
|  | 6. Tripping and closing characteristics |  |  |  |  |
|  | • Rated short circuit breaking current |  |  |  |  |
|  | • Rated short circuit breaking current |  | kA | 40 |  |
|  | - time constant of the asymmetric component (dc) of the rated short circuit current |  | ms | 45 |  |
|  | • Fault at the HV terminals of the CB - rated transient recovery voltage with |  |  |  |  |
|  | - first-pole-to-clear-factor |  |  | 1.5 |  |
|  | 7. Operation durations |  |  |  |  |
|  | • Maximum closing time |  | ms | < 150 |  |
|  | • Maximum breaking time |  | ms | < 40 |  |
|  | • After a complete operating sequence O-0,3s-CO- 3min-CO, the operating mechanism should have enough energy left to proceed one more CO cycle within |  | s | Specify |  |
|  | 8. Technical characteristics of the auxiliary circuits |  |  |  |  |
|  | • Operating voltage of the closing circuits |  |  |  |  |
|  | - voltage |  | Vdc | 220 |  |
|  | - operating range |  | % | 85 to 110 |  |
|  | • Operating voltage of the tripping coils |  |  |  |  |
|  | - voltage |  | Vdc | 220 |  |
|  | - operating range |  | % | 70 to 110 |  |
|  | • Operating voltage of the motor |  |  |  |  |
|  | - voltage |  | Vdc | 220 |  |
|  | - operating range |  | % | 85 to 110 |  |
|  | • Voltage of the heating circuits |  | Vac | 230 |  |
|  | 9. Operating mechanism of the CB |  |  |  |  |
|  | • Three pole operated |  |  | Three pole |  |
|  | • Type (energy) |  |  | Spring |  |
|  | • Number of closing coils |  |  | 2 |  |
|  | • Number of trip coils |  |  | 2 |  |
|  | - number of free of potential open contacts (NO) |  |  | min. 5, specify |  |
|  | - number of free of potential close contacts (NC) |  |  | min. 5, specify |  |

| TECHNICAL SCHEDULE – Data for Information Three phase Circuit Breaker – 110 kV – Three pole operated |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Description |  |  | Units | Imposed Values | Guaranteed Values* |
|  | 1. General characteristics |  |  |  |  |
|  | • Place of manufacture |  |  | Specify |  |
|  | • Standards (latest edition) |  |  | IEC 62271-100 IEC 62271-1 |  |
|  | • First-pole-to-clear-factor |  |  | 1.5 |  |
|  | • Rated operating sequence O-0,3s-CO-3min-CO |  |  | Yes |  |
|  | • Number of grading capacitor per pole |  |  | N.A. |  |
|  | • Type of CB operating mechanism |  |  | Specify |  |
|  | 2. Circuit breaker class |  |  |  |  |
|  | • CB mechanicam life classidication |  |  | M1 |  |
|  | • CB electrical life classiffication |  |  | E1 |  |
|  | • CB restrike probability classification |  |  | C1 |  |
|  | 3. Normal service conditions(please refer to the site conditions of each substation) |  |  |  |  |
|  | • Ambient temperature range |  | °C |  |  |
|  | • Relative humidity |  | % |  |  |
|  | • Maximum altitude |  | m |  |  |
|  | • Maximum ice coating |  | mm |  |  |
|  | • Maximum pressure of the wind speed |  | Pa |  |  |
|  | • Solar radiation |  | W/m² |  |  |
|  | 5. Overload capabilities |  |  |  |  |
|  | • Permissible overload currents in accordance with the standard IEC 62271-1 |  |  | Yes |  |
|  | 6. Rated voltage and rated insulation level |  |  |  |  |
|  | • Radio disturbance voltage at 1.1 U / -1MHz |  | μV | ≤ 2500 max. |  |
|  | 7. Tripping and closing characteristics |  |  |  |  |
|  | • Rated short circuit breaking current |  |  |  |  |
|  | - minimum opening time (m.o.t) |  | ms | Specify |  |
|  | - percentage of the asymmetric component ( at 10 ms + m.o.t) |  | % | Specify |  |
|  | - total I |  | kA | Specify |  |
|  | • Fault at the HV terminals of the CB - rated transient recovery voltage with |  |  |  |  |
|  | - rate of rise of recovery voltage (RRRV) |  | kV/µs | 2 |  |
|  | - transient recovery voltage peak value |  | kV | 211 |  |
|  | • Rated peak short circuit making current |  | kA peak | 100 |  |
|  | • On HV line, close fault occuring - rated transient recovery voltage |  |  |  |  |
|  | - fault on line side |  |  |  |  |
|  | . full wave impedance |  | Ω | 450 |  |
|  | . rate of rise factor of the recovery voltage |  | kV/μs.kA | 0,2 |  |
|  | . rated peak factor |  |  | 1,6 |  |
|  | - fault at source side (according IEC 56, table IV) |  |  |  |  |
|  | . rate of rise of recovery voltage |  | kV/µs | 2 |  |
|  | . peak value of the transient recovery voltage |  | kV | 141 |  |
|  | • Rated out-of-phase breaking current in discripency with a rated recovery voltage 2 x U /. |  | kA | 6.75 |  |
|  | • Rated line-charging breaking current (no load) |  |  |  |  |
|  | - rated short-circuit breaking current |  | A | 31.5. |  |
|  | - maximum overvoltage guarented without arcing |  | kV peak | < 2.5 x 100 |  |
|  | • Rated cable-charging breaking current no load) |  |  |  |  |
|  | - rated short-circuit breaking current |  | A | 140. |  |
|  | - maximum overvoltage guarented without arcing |  | kV peak | < 2.5 x 100 |  |
|  | • Rated maximum capacitive breaking current |  |  |  |  |
|  | - rated short-circuit breaking current |  | A | 400. |  |
|  | - maximum overvoltage guarented without arcing |  | kV peak | < 2.5 x 100 |  |
|  | • Rated small inductive breaking current |  |  |  |  |
|  | - rated short-circuit breaking current |  | A | Specify. |  |
|  | - maximum overvoltage guarented without arcing |  | kV peak | < 2.5 x 100 |  |
|  | • Number of operations taking into account the maintenance program specified by the manufacturer |  |  | min.2000 (class M1) |  |
|  | 8. Operation durations |  |  |  |  |
|  | • Maximum opening time |  | ms | Specify |  |
|  | • Maximum dead time (between break and restore) |  | ms | Specify |  |
|  | • Maximum discrepancy between |  |  |  |  |
|  | - the breaking chamber of a same pole |  |  |  |  |
|  | . during closing operation |  | ms | N.A. |  |
|  | . during opening operation |  | ms | N.A. |  |
|  | - the poles of different phases |  |  |  |  |
|  | . during closing operation |  | ms | 5 |  |
|  | . during opening operation |  | ms | 3.33 |  |
|  | • Minimal duration of the switching impuls for |  |  |  |  |
|  | - closing coil |  | ms | Specify |  |
|  | - trip coil |  | ms | Specify |  |
|  | 9. Technical characteristics of the auxiliary circuits |  |  |  |  |
|  | • Power consumption |  |  |  |  |
|  | - closing coil |  | W | Specify |  |
|  | - tripping coil |  | W | Specify |  |
|  | - motor of the operating mechanism |  | W | Specify |  |
|  | - continuous heating |  | W | Specify |  |
|  | - heating with thermostat |  | W | Specify |  |
|  | 10. Breaking chamber |  |  |  |  |
|  | • Quenching fluid |  |  | SF6 |  |
|  | - Filling in pressure |  | MPa (abs) | Specify |  |
|  | - first alarm pressure |  | MPa (abs) | Specify |  |
|  | - second alarm pressur (lockout or trip) |  | MPa (abs) | Specify |  |
|  | • Number of breaking chamber per poles of the CB |  |  | 1 |  |
|  | • Rated value of the grading capacitor |  | pF | N.A. |  |
|  | • Gas quantity per pole of the CB |  | kg | Specify |  |
|  | • Total course of the moving contact in one breaking chamber |  | mm | Specify |  |
|  | • Distance between the mains contact in one breaking chamber |  | mm | Specify |  |
|  | • Operating speed of the moving contact |  |  |  |  |
|  | - closing time |  | m/s | Specify |  |
|  | - breaking time |  | m/s | Specify |  |
|  | • Densimeter of temperature compensated manometer (SF6 monitoring) |  |  | 1 by pole |  |
|  | • Overpressure valve |  |  | Specify |  |
|  | 11. Operating mechanism of the CB |  |  |  |  |
|  | • Type of operating mechanism |  |  | Specify |  |
|  | • Manufacturer reference |  |  |  |  |
|  | • Energy |  |  | Mechanical |  |
|  | • Auxiliary position contacts |  |  |  |  |
|  | - double opening type |  |  | Yes |  |
|  | - rated continuous current (class 1) |  | A | 10 |  |
|  | - rated capacity |  | A | 4A/220V |  |
|  | • Operations counter |  |  | Yes |  |
|  | • In/Out push button |  |  |  |  |
|  | - electrical |  |  | No |  |
|  | - mechanical |  |  | Yes |  |
|  | • Corrosion protection of the CB control cabinet |  |  | Galvanised |  |
|  | • IP protection degree |  |  | ≥ IP55 |  |
|  | 12. Isolator characteristics |  |  |  |  |
|  | • Manufacturer |  |  | Specify |  |
|  | • Type |  |  | Specify |  |
|  | • Used material |  |  | Ceramic |  |
|  | • Insulated shed profile |  |  | Specify |  |
|  | • Between protective cover or lower terminal and earth |  |  |  |  |
|  | - Number of elements |  |  | 1 |  |
|  | - Total height |  | mm | Specify |  |
|  | - Minimum creeping distance |  | mm/kV | 31 |  |
|  | • Between entrance and exit |  |  |  |  |
|  | - number of elements |  |  | 1 |  |
|  | - total height |  | mm | Specify |  |
|  | - Minimum creeping distance |  | mm/kV | 31 |  |
|  | 13. Mechanical characteristics |  |  |  |  |
|  | • Weight of the CB |  | kg | Specify |  |
|  | • Weight of the CB operating cabinet |  | kg | Specify |  |
|  | • Minimum clearance between 2 different phases |  | mm | Specify |  |
|  | • HV connection terminals made of bored aluminium plates |  |  | Yes |  |
|  | 14. Paint and corrosion protection |  |  |  |  |
|  | • Oxydable metal parts |  |  | hot dip galvanizing |  |
|  | • Screws, nuts, bolts,…. |  |  |  |  |
|  | - for diameter ≤ M16 stainless steel |  |  | Yes |  |
|  | - for diameter > M16 hot dip galvanized steel and painted |  |  | Yes |  |
|  | • Frame of control panel galvanized |  |  | Yes |  |
|  | • Duplex principle (galvanized + paint) according GTS |  |  | Yes |  |
|  | • Final color paint |  |  |  |  |
|  | - pieces to earth |  |  | Specify |  |
|  | - live parts |  |  | Specify |  |
|  | - insulator's metal flanges |  |  | Specify |  |
|  | - grounded connections, metallic conductors,… free of paint |  |  |  |  |
|  |  |  |  |  |  |
|  | 15. Documents to be submitted |  |  |  |  |
|  | • Submital fase |  |  | 3 ex. |  |
|  | - General documentation |  |  |  |  |
|  | - List of references |  |  |  |  |
|  | - Type test reports |  |  |  |  |
|  | - datasheet completed |  |  |  |  |
|  | - dimensional drawing |  |  |  |  |
|  | • Ordering fase |  |  | 3 ex. |  |
|  | - operating instruction manual |  |  |  |  |
|  | - erection instruction manual |  |  |  |  |
|  | - maintenance instruction manual |  |  |  |  |
|  | - static and dynamic efforts |  |  |  |  |
|  | - drawings |  |  |  |  |
|  | - detailed dimensional drawing with an indication of weight and efforts |  |  |  |  |
|  | - drawing of the operating cabinet |  |  |  |  |
|  | - drawing of the supporting structure (eventual) |  |  |  |  |
|  | - drawing of the rating plate |  |  |  |  |
|  | - LV diagrams |  |  |  |  |
|  | - drawing of electrical circuits |  |  |  |  |
|  | - principle diagram of the operating mechanism |  |  |  |  |
|  | • Completed Manufactuer final report including |  |  | 3 ex. |  |
|  | - operating instruction manual |  |  |  |  |
|  | - erection instruction manual |  |  |  |  |
|  | - maintenance instruction manual |  |  |  |  |
|  | - as built drawings and schematics |  |  |  |  |
|  | - factory test report |  |  |  |  |
|  | - report end assembly and testing on site |  |  |  |  |
|  | 16. Languages |  |  |  |  |
|  | • All documents establish in English |  |  | Yes |  |

| TECHNICAL SCHEDULE – Main Data Inductive Current Transformer 110kV |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Description |  |  | Units | Imposed Values | Guaranteed Values |
|  | 1. General characteristics |  |  |  |  |
|  | • Manufacturer |  |  | Specify |  |
|  | • Type |  |  | Single phase , oil immersed, Inductive |  |
|  | • Indoor/Outdoor installation |  |  | Outdoor |  |
|  | 2. Normal service conditions |  |  |  |  |
|  | • Ambient temperature range |  | °C | -35 to +50 |  |
|  | 3. Electrical characteristics |  |  |  |  |
|  | • Rated Frequency |  | Hz | 50 |  |
|  | • Service voltage |  | kV | 110 |  |
|  | • Rated voltage (Ur) |  | kV | 126 |  |
|  | • Rated short duration power-frequency withstand voltage (AC) 1min-50Hz (Ud) |  | kV | 230 |  |
|  | • Rated lightning impulse withstand voltage (Up) |  | kV peak | 550 |  |
|  | • Rated short time withstand current (1s) |  | kA | 31.5 |  |
|  | • Rated peak withstand current |  | kA | 82 |  |
|  | • Permanently permissible primary overcurrent |  |  | 1.2 In |  |
|  | • Secondary windings |  |  |  |  |
|  | - Secondary nominal current |  | A | 5 |  |
|  | - Rated insulation voltage |  | kV | 0.72 |  |
|  | - Short duration power-frequency withstand voltage (AC) 1min-50Hz |  | kV | 3 |  |
|  | 4. Windings characteristics |  |  |  |  |
|  | • Turn ratio |  |  |  |  |
|  | - Core nr.1 (metering) |  | A | 200-400-600 |  |
|  | - Core nr.2 (measure) |  | A | 200-400-600 |  |
|  | - Core nr.3 (protection) |  | A | 200-400-600 |  |
|  | - Core nr.4 (protection) |  | A | 200-400-600 |  |
|  | - Core nr.5 (protection) |  | A | 200-400-600 |  |
|  | • Accuracy burden |  |  |  |  |
|  | - Core nr.1 (metering) |  | VA | 50 |  |
|  | - Core nr.2 (measure) |  | VA | 50 |  |
|  | - Core nr.3 (protection) |  | VA | 50 |  |
|  | - Core nr.4 (protection) |  | VA | 50 |  |
|  | - Core nr.5 (protection) |  | VA | 50 |  |
|  | • Accuracy class |  |  |  |  |
|  | - Core nr.1 (metering) |  |  | 0.2Fs5 |  |
|  | - Core nr.2 (measure) |  |  | 0.5Fs5 |  |
|  | - Core nr.3 (protection - 5P) |  |  | 5P30 |  |
|  | - Core nr.4 (protection - 5P) |  |  | 5P30 |  |
|  | - Core nr.5 (protection - 5P) |  |  | 5P30 |  |
|  | 5. Insulators characteritics |  |  |  |  |
|  | • Used material |  |  | Porcelain – Brown |  |
|  | • Manufacturer |  |  | Specify |  |
|  | • Number of elements |  |  | 1 |  |
|  | • Minimum nominal creeping distance |  | mm | 3906 |  |

| TECHNICAL SCHEDULE – Data for Information Inductive Current Transformer 110kV |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Description |  |  | Units | Imposed Values | Guaranteed Values |
|  | 1. General characteristics |  |  |  |  |
|  | • Place of manufacture |  |  | Specify |  |
|  | • Type |  |  | Specify |  |
|  | • Standards (latest edition) |  |  | IEC 61869-1 and 2 |  |
|  | 2. Normal service conditions(please refer to the site conditions of each substation) |  |  |  |  |
|  | • Ambient temperature range |  | °C |  |  |
|  | • Relative humidity |  | % |  |  |
|  | • Maximum altitude |  | m |  |  |
|  | • Maximum ice coating |  | mm |  |  |
|  | • Maximum pressure of the wind speed |  | Pa |  |  |
|  | • Solar radiation |  | W/m² |  |  |
|  | 3. Overload conditions |  |  |  |  |
|  | • Permissible overload currents in accordance with the standard IEC 62271-1 |  |  | Yes |  |
|  | 4. Electromagnetic Unit |  |  |  |  |
|  | • Internal insulation |  |  | Specify |  |
|  | • Oil |  |  |  |  |
|  | - type |  |  | Specify |  |
|  | - supplier and oil reference |  |  | Specify |  |
|  | • Hermeticity type system |  |  | Specify |  |
|  | 5. Mechanical characteristics |  |  |  |  |
|  | • Total height |  | mm | Specify |  |
|  | • Total weight |  | kg | Specify |  |
|  | • Oil weight |  | kg | Specify |  |
|  | • Primary terminals |  |  |  |  |
|  | - alloy |  |  | Tinned copper |  |
|  | - diameter |  | mm | Specify |  |
|  | - Contact length |  | mm | Specify |  |
|  | - Height (axis ground surface - primary terminal) |  | mm | Specify |  |
|  | • Secondary terminals |  |  |  |  |
|  | - Earthing bar and removable bridges |  |  | Yes |  |
|  | 6. Paint and corrosion protection |  |  |  |  |
|  | • Oxydable metal parts |  |  | hot dip galvanizing |  |
|  | • Screws, nuts, bolts,…. |  |  |  |  |
|  | - for diameter ≤ M16 stainless steel |  |  | Yes |  |
|  | - for diameter > M16 hot dip galvanized steel and painted |  |  | Yes |  |
|  | • Frame of control panel galvanized |  |  | Yes |  |
|  | • Duplex principle (galvanized + paint) according GTS |  |  | Yes |  |
|  | • Final color paint |  |  |  |  |
|  | - pieces to earth |  |  | Specify |  |
|  | - live parts |  |  | Specify |  |
|  | - insulator's metal flanges |  |  | Specify |  |
|  | - grounded connections, metallic conductors,… free of paint |  |  |  |  |
|  | 7. Documents to be submitted |  |  |  |  |
|  | • Submital fase |  |  | 3 ex. |  |
|  | - General documentation |  |  |  |  |
|  | - List of references |  |  |  |  |
|  | - Type test reports |  |  |  |  |
|  | - datasheet completed |  |  |  |  |
|  | - dimensional drawing |  |  |  |  |
|  | • Ordering fase |  |  | 3 ex. |  |
|  | - erection instruction manual |  |  |  |  |
|  | - maintenance instruction manual |  |  |  |  |
|  | - static and dynamic efforts |  |  |  |  |
|  | - drawings |  |  |  |  |
|  | - detailed dimensional drawing with an indication of weight and efforts |  |  |  |  |
|  | - drawing of the LV terminals cabinet |  |  |  |  |
|  | - drawing of the rating plate |  |  |  |  |
|  | • Completed Manufactuer final report including |  |  | 3 ex. |  |
|  | - erection instruction manual |  |  |  |  |
|  | - maintenance instruction manual |  |  |  |  |
|  | - as built drawings and schematics |  |  |  |  |
|  | - factory test report |  |  |  |  |
|  | 8. Languages |  |  |  |  |
|  | • All documents establish in English |  |  | Yes |  |

| TECHNICAL SCHEDULE – Main Data Disconnector 1 Pole - 110kV |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Description |  |  | Units | Imposed Values | Guaranteed Values* |
|  | 1. General characteristics |  |  |  |  |
|  | • Manufacturer |  |  | Specify |  |
|  | • Type |  |  | Specify |  |
|  | • Number of poles |  |  | 1 |  |
|  | • Indoor/Outdoor installation |  |  | Outdoor |  |
|  | • Maximum opening time |  | s | 10 |  |
|  | • Maximum closing time |  | s | 10 |  |
|  | • Number of switching events until the first maintenance |  |  | 1000 |  |
|  | • Insulator type |  |  | Brown Porcelain |  |
|  | • Minimum nominal creeping distance |  | mm / kV | 31 |  |
|  | 2. Normal service conditions |  |  |  |  |
|  | • Ambient temperature range |  | °C | -35 to +50 |  |
|  | 3. Currents characteristics |  |  |  |  |
|  | • Rated bus transfer current |  | A | 1250 |  |
|  | • Rated line bay |  | A | 800 |  |
|  | • Rated autotransformer bay |  | A | 1250 |  |
|  | • Rated buscoupler bay |  | A | 2500 |  |
|  | • Rated short time withstand current |  | kA | 40 |  |
|  | • Rated peak withstand current |  | kA peak | 100 |  |
|  | • Rated duration of short circuit |  | s | 3 |  |
|  | 4. Rated voltage and rated insulation level |  |  |  |  |
|  | • Network nominal voltage |  | kV | 110 |  |
|  | • Rated voltage (Ur) |  | kV | 126 |  |
|  | • Rated frequency |  | Hz | 50 |  |
|  | • Rated duration short-duration power-frequency withstand voltage (Ud) |  |  |  |  |
|  | - Phase to earth |  | kV | 230 |  |
|  | - Across open switching device |  | kV | 265 |  |
|  | • Rated lightning impulse withstand voltage (1,2/50µs) (Up) |  |  |  |  |
|  | - Phase to earth |  | kV peak | 550 |  |
|  | - Across open switching device |  | kV peak | 630 |  |
|  | 5. Operating device |  |  |  |  |
|  | • Type of operating device |  |  |  |  |
|  | - Single operated |  |  | YES |  |
|  | - Motorized or manual operated |  |  | motorized |  |
|  | • Motorization |  |  |  |  |
|  | - Rated voltage of the motor |  | Vdc | 220 |  |
|  | • Number of potential free auxiliary contacts |  |  |  |  |
|  | - Closed – Open - Open: COO |  |  | 4 |  |
|  | - Open – Open - Closed: OOC |  |  | 4 |  |
|  | - Open – Closed - Closed: OCC |  |  | 2 |  |
|  | - Open – Closed - Open: OCO |  |  | 2 |  |
|  | • Heating |  |  |  |  |
|  | - Rated voltage |  | Vca | 230 |  |

| TECHNICAL SCHEDULE – Data for Information Disconnector 1 Pole - 110kV |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Description |  |  | Units | Imposed Values | Guaranteed Values* |
|  | 1. General characteristics |  |  |  |  |
|  | • Place of manufacture |  |  | Specify |  |
|  | • Type |  |  | Specify |  |
|  | • Standards (latest edition) |  |  | IEC 62271-102 |  |
|  | • Class |  |  |  |  |
|  | - Main blades |  |  | M1 |  |
|  | 2. Normal service conditions(please refer to the site conditions of each substation) |  |  |  |  |
|  | • Ambient temperature range |  | °C |  |  |
|  | • Relative humidity |  | % |  |  |
|  | • Maximum altitude |  | m |  |  |
|  | • Maximum ice coating |  | mm |  |  |
|  | • Maximum pressure of the wind speed |  | Pa |  |  |
|  | • Solar radiation |  | W/m² |  |  |
|  | 3. Currents characteristics |  |  |  |  |
|  | • Maximum temperature rise at In (t° ambient: 45°C) |  |  | Specify |  |
|  | 4. Rated voltage and rated insulation level |  |  |  |  |
|  | • Contact resistance |  | μΩ | Specify |  |
|  | 5. Overload conditions |  |  |  |  |
|  | • Permissible overload currents in accordance with the standard IEC 62271-1 |  |  | Yes |  |
|  | 6. Isolators |  |  |  |  |
|  | • Manufacturer |  |  | Specify |  |
|  | • Type (based IEC) |  |  | Specify |  |
|  | • Height |  | mm | Specify |  |
|  | • Weight |  | kg | Specify |  |
|  | • Number of elements |  |  | 1 |  |
|  | • Profile |  |  | Specify |  |
|  | 7. Operating device |  |  |  |  |
|  | • Type (manufacturer reference) |  |  | Specify |  |
|  | - Three pole operated cabinet |  |  | No |  |
|  | - Single pole operated cabinet |  |  | Yes |  |
|  | - Motorized or manual operated |  |  | motorized |  |
|  | • Motorization |  |  |  |  |
|  | - Rated voltage of the motor |  | Vdc | 220 |  |
|  | - Tolerance |  | % | 85 - 110 |  |
|  | - Capacity |  | W | Specify |  |
|  | - Motor current |  | A | Specify |  |
|  | - Maximum motor current |  | A | Specify |  |
|  | - Rated current for operation at maximum torque |  | A | Specify |  |
|  | - Switching time: |  |  |  |  |
|  | - Closing time of the disconnector |  | s | Specify |  |
|  | - Opening time of the disconnector |  | s | Specify |  |
|  | • Emergency manual operating device available |  |  |  |  |
|  | - Type of operating device (crank,….) |  |  | Specify |  |
|  | - Maximal torque needed for manual opening |  | Nm | Specify |  |
|  | - Maximal torque needed for manual closing |  | Nm | Specify |  |
|  | - Maximal operation height above ground level |  | mm | 1500 |  |
|  | • Number of potential free auxiliary contacts |  |  |  |  |
|  | - Breaking capacity |  |  | 4 A at 220 V |  |
|  | - Minimum rated current |  |  | 10 A (class 1) |  |
|  | • Heating |  |  |  |  |
|  | - Rated voltage |  | Vca | 230 |  |
|  | - Tolerance |  | % | 85 - 110 |  |
|  | - Power |  | W | Specify |  |
|  | • Protection level |  |  | ≥IP 55 |  |
|  | 8. Safety and locking |  |  |  |  |
|  | • Normal electrical operated mechanism |  |  |  |  |
|  | - Mechanical locking device placed on motor drive |  |  | Yes |  |
|  | - Motor circuit interrupted by the locking device |  |  | Yes |  |
|  | - Padlockable mechanical locking device in open and closed position (padlocking Ø8mm possible) |  |  | Yes |  |
|  | • Manual drive (if applicable) |  |  | N.A. |  |
|  | - Locking coil in combination with push button |  |  | N.A. |  |
|  | - Supply voltage |  | Vdc | N.A. |  |
|  | - Padlockable mechanical locking device in open and closed position (padlocking Ø8mm possible) |  |  | N.A. |  |
|  | 9. Ergonomics |  |  |  |  |
|  | • Minimum height from ground or circulation level |  |  |  |  |
|  | - bottom skirt of the isolator |  | mm | 2500 |  |
|  | - vertical distance of life part |  | mm | 4500 |  |
|  | • Preferential height from ground or circulation level |  |  |  |  |
|  | - bottom side of the drives |  | mm | 1000 < H < 1600 |  |
|  | - top side of the drives |  | mm | Maximum 2500 |  |
|  | - door handles |  | mm | Maximum 1800 |  |
|  | 10. Mechanical characteristics |  |  |  |  |
|  | • Weight of the complete disconnector |  | kg | Specify |  |
|  | • Weight of the operating mechanism |  |  |  |  |
|  | - Weight of the three pole operating mechanism |  | kg | N.A. |  |
|  | - Weight of the single pole operating mechanism |  | kg | Specify |  |
|  | - Weight of the central control cubicle |  | kg | Specify |  |
|  | 11. Construction details |  |  |  |  |
|  | • Main blades |  |  |  |  |
|  | - Used material for contact (Al, electroplated silver or tinned copper, others) |  |  | Specify |  |
|  | - Contact type |  |  | Specify |  |
|  | - Maximum temperature rise at In (t° ambient: 45°C) |  |  | Specify |  |
|  | - Number of contact fingers |  |  | Specify |  |
|  | - Contact pressure by finger |  | daN | Specify |  |
|  | - Type of electrical connection between elements |  |  | Specify |  |
|  | • HV Terminals |  |  |  |  |
|  | - Diameter (according Inom) |  |  | Specify |  |
|  | - Used material for contact (Al, electroplated silver or tinned copper) |  |  | Specify |  |
|  | - Length |  |  | Specify |  |
|  | - Supply all the parts needed for connecting connection (including connectors on the busbar) |  |  | Yes |  |
|  | 12. Paint and corrosion protection |  |  |  |  |
|  | • Oxydable metal parts |  |  | hot dip galvanizing |  |
|  | • Screws, nuts, bolts,…. |  |  |  |  |
|  | - for diameter ≤ M16 stainless steel |  |  | Yes |  |
|  | - for diameter > M16 hot dip galvanized steel and painted |  |  | Yes |  |
|  | • Frame of control panel galvanized |  |  | Yes |  |
|  | • Duplex principle (galvanized + paint) according GTS |  |  | Yes |  |
|  | • Final color paint |  |  |  |  |
|  | - pieces to earth |  |  | Specify |  |
|  | - live parts |  |  | Specify |  |
|  | - insulator's metal flanges |  |  | Specify |  |
|  | - grounded connections, metallic conductors,… free of paint |  |  |  |  |
|  |  |  |  |  |  |
|  | 13. Documents to be submitted |  |  |  |  |
|  | • Submital fase |  |  | 3 ex. |  |
|  | - General documentation |  |  |  |  |
|  | - List of references |  |  |  |  |
|  | - Type test reports |  |  |  |  |
|  | - datasheet completed |  |  |  |  |
|  | - dimensional drawing |  |  |  |  |
|  | • Ordering fase |  |  | 3 ex. |  |
|  | - operating instruction manual |  |  |  |  |
|  | - erection instruction manual |  |  |  |  |
|  | - maintenance instruction manual |  |  |  |  |
|  | - static and dynamic efforts |  |  |  |  |
|  | - drawings |  |  |  |  |
|  | - detailed dimensional drawing with an indication of weight and efforts |  |  |  |  |
|  | - drawing of the operating cubicle |  |  |  |  |
|  | - drawing of the rating plate |  |  |  |  |
|  | - LV diagrams |  |  |  |  |
|  | - drawing of electrical circuits |  |  |  |  |
|  | - principle diagram of the operating mechanism |  |  |  |  |
|  | • Completed Manufactuer final report including |  |  | 3 ex. |  |
|  | - operating instruction manual |  |  |  |  |
|  | - erection instruction manual |  |  |  |  |
|  | - maintenance instruction manual |  |  |  |  |
|  | - as built drawings and schematics |  |  |  |  |
|  | - factory test report |  |  |  |  |
|  | 14. Languages |  |  |  |  |
|  | • All documents establish in English |  |  | Yes |  |

| TECHNICAL SCHEDULE – Main Data Disconnector 3 Poles - 110kV |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Description |  |  | Units | Imposed Values | Guaranteed Values* |
|  | 1. General characteristics |  |  |  |  |
|  | • Manufacturer |  |  | Specify |  |
|  | • Type |  |  | Specify |  |
|  | • Number of poles |  |  | 3 |  |
|  | • Indoor/Outdoor installation |  |  | Outdoor |  |
|  | • Maximum opening time |  | s | 10 |  |
|  | • Maximum closing time |  | s | 10 |  |
|  | • Number of switching events until the first maintenance |  |  | 1000 |  |
|  | • Insulator type |  |  | Brown Porcelain |  |
|  | • Minimum nominal creeping distance |  | mm / kV | 31 |  |
|  | 2. Normal service conditions |  |  |  |  |
|  | • Ambient temperature range |  | °C | -35 to +50 |  |
|  | 3. Currents characteristics |  |  |  |  |
|  | • Rated bus transfer current |  | A | 1250 |  |
|  | • Rated line bay |  | A | 800 |  |
|  | • Rated autotransformer bay |  | A | 1250 |  |
|  | • Rated buscoupler bay |  | A | 2500 |  |
|  | • Rated short time withstand current |  | kA | 40 |  |
|  | • Rated peak withstand current |  | kA peak | 100 |  |
|  | • Rated duration of short circuit |  | s | 3 |  |
|  | 4. Rated voltage and rated insulation level |  |  |  |  |
|  | • Network nominal voltage |  | kV | 110 |  |
|  | • Rated voltage (Ur) |  | kV | 123 |  |
|  | • Rated frequency |  | Hz | 50 |  |
|  | • Rated duration short-duration power-frequency withstand voltage (Ud) |  |  |  |  |
|  | - Phase to earth |  | kV | 230 |  |
|  | - Across open switching device |  | kV | 265 |  |
|  | • Rated lightning impulse withstand voltage (1,2/50µs) (Up) |  |  |  |  |
|  | - Phase to earth |  | kV peak | 550 |  |
|  | - Across open switching device |  | kV peak | 630 |  |
|  | 5. Operating device |  |  |  |  |
|  | • Type of operating device |  |  |  |  |
|  | - Single or three pole operated |  |  | single |  |
|  | - Motorized or manual operated |  |  | motorized |  |
|  | • Motorization |  |  |  |  |
|  | - Rated voltage of the motor |  | Vdc | 220 |  |
|  | • Number of potential free auxiliary contacts |  |  |  |  |
|  | - Closed – Open - Open: COO |  |  | 4 |  |
|  | - Open – Open - Closed: OOC |  |  | 4 |  |
|  | - Open – Closed - Closed: OCC |  |  | 2 |  |
|  | - Open – Closed - Open: OCO |  |  | 2 |  |
|  | • Heating |  |  |  |  |
|  | - Rated voltage |  | Vca | 230 |  |

| TECHNICAL SCHEDULE – Data for Information Disconnector 3 Poles - 110kV |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Description |  |  | Units | Imposed Values | Guaranteed Values* |
|  | 1. General characteristics |  |  |  |  |
|  | • Place of manufacture |  |  | Specify |  |
|  | • Standards (latest edition) |  |  | IEC 62271-102 |  |
|  | • Class |  |  |  |  |
|  | - Main blades |  |  | M1 |  |
|  | 2. Normal service conditions(please refer to the site conditions of each substation) |  |  |  |  |
|  | • Ambient temperature range |  | °C |  |  |
|  | • Relative humidity |  | % |  |  |
|  | • Maximum altitude |  | m |  |  |
|  | • Maximum ice coating |  | mm |  |  |
|  | • Maximum pressure of the wind speed |  | Pa |  |  |
|  | • Solar radiation |  | W/m² |  |  |
|  | 3. Currents characteristics |  |  |  |  |
|  | • Maximum temperature rise at In (t° ambient: 45°C) |  |  | Specify |  |
|  | 4. Rated voltage and rated insulation level |  |  |  |  |
|  | • Contact resistance |  | μΩ | Specify |  |
|  | 5. Overload conditions |  |  |  |  |
|  | • Permissible overload currents in accordance with the standard IEC 62271-1 |  |  | Yes |  |
|  | 6. Isolators |  |  |  |  |
|  | • Manufacturer |  |  | Specify |  |
|  | • Type (based IEC) |  |  | Specify |  |
|  | • Height |  | mm | Specify |  |
|  | • Weight |  | kg | Specify |  |
|  | • Number of elements |  |  | 1 |  |
|  | • Profile |  |  | Specify |  |
|  | 7. Operating device |  |  |  |  |
|  | • Type (manufacturer reference) |  |  | Specify |  |
|  | - Three pole operated cabinet |  |  | No |  |
|  | - Single pole operated cabinet (3 cabinets) + 1 central control cubicle |  |  | Yes |  |
|  | - Motorized or manual operated |  |  | motorized |  |
|  | • Motorization |  |  |  |  |
|  | - Rated voltage of the motor |  | Vdc | 220 |  |
|  | - Tolerance |  | % | 85 - 110 |  |
|  | - Capacity |  | W | Specify |  |
|  | - Motor current |  | A | Specify |  |
|  | - Maximum motor current |  | A | Specify |  |
|  | - Rated current for operation at maximum torque |  | A | Specify |  |
|  | - Switching time: |  |  |  |  |
|  | - Closing time of the disconnector |  | s | Specify |  |
|  | - Opening time of the disconnector |  | s | Specify |  |
|  | • Emergency manual operating device available |  |  |  |  |
|  | - Type of operating device (crank,….) |  |  | Specify |  |
|  | - Maximal torque needed for manual opening |  | Nm | Specify |  |
|  | - Maximal torque needed for manual closing |  | Nm | Specify |  |
|  | - Maximal operation height above ground level |  | mm | 1500 |  |
|  | • Number of potential free auxiliary contacts |  |  |  |  |
|  | - Closed – Open - Open: COO |  |  | 4 |  |
|  | - Open – Open - Closed: OOC |  |  | 4 |  |
|  | - Open – Closed - Closed: OCC |  |  | 2 |  |
|  | - Open – Closed - Open: OCO |  |  | 2 |  |
|  | - Breaking capacity |  |  | 4 A at 220 V |  |
|  | - Minimum rated current |  |  | 10 A (class 1) |  |
|  | • Heating |  |  |  |  |
|  | - Rated voltage |  | Vca | 230 |  |
|  | - Tolerance |  | % | 85 - 110 |  |
|  | - Power |  | W | Specify |  |
|  | • Protection level |  |  | ≥IP 55 |  |
|  | 8. Safety and locking |  |  |  |  |
|  | • Normal electrical operated mechanism |  |  |  |  |
|  | - Mechanical locking device placed on motor drive |  |  | Yes |  |
|  | - Motor circuit interrupted by the locking device |  |  | Yes |  |
|  | - Padlockable mechanical locking device in open and closed position (padlocking Ø8mm possible) |  |  | Yes |  |
|  | • Manual drive (if applicable) |  |  | N.A. |  |
|  | - Locking coil in combination with push button |  |  | N.A. |  |
|  | - Supply voltage |  | Vdc | N.A. |  |
|  | - Padlockable mechanical locking device in open and closed position (padlocking Ø8mm possible) |  |  | N.A. |  |
|  | 9. Ergonomics |  |  |  |  |
|  | • Minimum height from ground or circulation level |  |  |  |  |
|  | - bottom skirt of the isolator |  | mm | 2500 |  |
|  | - vertical distance of life part |  | mm | 4500 |  |
|  | • Preferential height from ground or circulation level |  |  |  |  |
|  | - bottom side of the drives |  | mm | 1000 < H < 1600 |  |
|  | - top side of the drives |  | mm | Maximum 2500 |  |
|  | - door handles |  | mm | Maximum 1800 |  |
|  | 10. Mechanical characteristics |  |  |  |  |
|  | • Weight of the complete disconnector |  | kg | Specify |  |
|  | • Weight of the operating mechanism |  |  |  |  |
|  | - Weight of the three pole operating mechanism |  | kg | N.A. |  |
|  | - Weight of the single pole operating mechanism |  | kg | Specify |  |
|  | - Weight of the central control cubicle |  | kg | Specify |  |
|  | 11. Construction details |  |  |  |  |
|  | • Main blades |  |  |  |  |
|  | - Used material for contact (Al, electroplated silver or tinned copper, others) |  |  | Specify |  |
|  | - Contact type |  |  | Specify |  |
|  | - Maximum temperature rise at In (t° ambient: 45°C) |  |  | Specify |  |
|  | - Number of contact fingers |  |  | Specify |  |
|  | - Contact pressure by finger |  | daN | Specify |  |
|  | - Type of electrical connection between elements |  |  | Specify |  |
|  | • HV Terminals |  |  |  |  |
|  | - Diameter (according Inom) |  |  | Specify |  |
|  | - Used material for contact (Al, electroplated silver or tinned copper) |  |  | Specify |  |
|  | - Length |  |  | Specify |  |
|  | - Supply all the parts needed for connecting connection (including connectors on the busbar) |  |  | Yes |  |
|  | 12. Paint and corrosion protection |  |  |  |  |
|  | • Oxydable metal parts |  |  | hot dip galvanizing |  |
|  | • Screws, nuts, bolts,…. |  |  |  |  |
|  | - for diameter ≤ M16 stainless steel |  |  | Yes |  |
|  | - for diameter > M16 hot dip galvanized steel and painted |  |  | Yes |  |
|  | • Frame of control panel galvanized |  |  | Yes |  |
|  | • Duplex principle (galvanized + paint) according GTS |  |  | Yes |  |
|  | • Final color paint |  |  |  |  |
|  | - pieces to earth |  |  | Specify |  |
|  | - live parts |  |  | Specify |  |
|  | - insulator's metal flanges |  |  | Specify |  |
|  | - grounded connections, metallic conductors,… free of paint |  |  |  |  |
|  |  |  |  |  |  |
|  | 13. Documents to be submitted |  |  |  |  |
|  | • Submital fase |  |  | 3 ex. |  |
|  | - General documentation |  |  |  |  |
|  | - List of references |  |  |  |  |
|  | - Type test reports |  |  |  |  |
|  | - datasheet completed |  |  |  |  |
|  | - dimensional drawing |  |  |  |  |
|  | • Ordering fase |  |  | 3 ex. |  |
|  | - operating instruction manual |  |  |  |  |
|  | - erection instruction manual |  |  |  |  |
|  | - maintenance instruction manual |  |  |  |  |
|  | - static and dynamic efforts |  |  |  |  |
|  | - drawings |  |  |  |  |
|  | - detailed dimensional drawing with an indication of weight and efforts |  |  |  |  |
|  | - drawing of the operating cubicle |  |  |  |  |
|  | - drawing of the rating plate |  |  |  |  |
|  | - LV diagrams |  |  |  |  |
|  | - drawing of electrical circuits |  |  |  |  |
|  | - principle diagram of the operating mechanism |  |  |  |  |
|  | • Completed Manufactuer final report including |  |  | 3 ex. |  |
|  | - operating instruction manual |  |  |  |  |
|  | - erection instruction manual |  |  |  |  |
|  | - maintenance instruction manual |  |  |  |  |
|  | - as built drawings and schematics |  |  |  |  |
|  | - factory test report |  |  |  |  |
|  | 14. Languages |  |  |  |  |
|  | • All documents establish in English |  |  | Yes |  |

| TECHNICAL SCHEDULE – Main Data |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Combinated Disconnector and Earthing - 110kV |  |  |  |  |  |
| Description |  |  | Units | Imposed Values | Guaranteed Values* |
|  | 1. General characteristics |  |  |  |  |
|  | • Manufacturer |  |  | Specify |  |
|  | • Type |  |  | Specify |  |
|  | • Number of poles |  |  | 3 |  |
|  | • Indoor/Outdoor installation |  |  | Outdoor |  |
|  | • Maximum opening time |  | s | 10 |  |
|  | • Maximum closing time |  | s | 10 |  |
|  | •Number of switching events until the first maintenance |  |  | 1000 |  |
|  | • Insulator type |  |  | Brown Porcelain |  |
|  | • Minimum nominal creeping distance |  | mm / kV | 31 |  |
|  | 2. Normal service conditions |  |  |  |  |
|  | • Ambient temperature range |  | °C | -35 to +50 |  |
|  | 3. Currents Characteristics |  |  |  |  |
|  | • Rated bus transfer current |  | A | 1250 |  |
|  | • Rated line bay current |  | A | 800 |  |
|  | • Rated autotransformer bay current |  | A | 1250 |  |
|  | • Rated buscoupler bay current |  | A | 2500 |  |
|  | • Rated short time withstand current |  | kA | 40 |  |
|  | • Rated peak withstand current |  | kA peak | 100 |  |
|  | • Rated duration of short circuit |  | s | 3 |  |
|  | 4. Rated voltage and rated insulation level |  |  |  |  |
|  | • Service voltage |  | kV | 110 |  |
|  | • Rated voltage (Ur) |  | kV | 123 |  |
|  | • Rated frequency |  | Hz | 50 |  |
|  | • Rated duration short-duration power-frequency withstand voltage (Ud) |  |  |  |  |
|  | - Phase to earth |  | kV | 230 |  |
|  | - Across open switching device |  | kV | 265 |  |
|  | • Rated lightning impulse withstand voltage (1,2/50µs) (Up) |  |  |  |  |
|  | - Phase to earth |  | kV peak | 550 |  |
|  | - Across open switching device |  | kV peak | 630 |  |
|  | • Weight |  | kg | Specify |  |
|  | 5. Disconnector operating device |  |  |  |  |
|  | Main blades |  |  |  |  |
|  | • Type of operating device |  |  |  |  |
|  | - Three or single pole operated |  |  | three pole |  |
|  | - Motorized or manual operated |  |  | motorized |  |
|  | • Motorization |  |  |  |  |
|  | - Rated voltage of the motor |  | Vdc | 220 |  |
|  | • Number of potential free auxiliary contacts |  |  |  |  |
|  | - Closed – Open - Open: COO |  |  | 4 |  |
|  | - Open – Open - Closed: OOC |  |  | 4 |  |
|  | - Open – Closed - Closed: OCC |  |  | 2 |  |
|  | - Open – Closed - Open: OCO |  |  | 2 |  |
|  | • Heating |  |  |  |  |
|  | - Rated voltage |  | Vca | 230 |  |
|  | Earth blades for lines |  |  |  |  |
|  | • Type of operating device |  |  |  |  |
|  | • Three or single pole operated |  |  | three pole |  |
|  | • Motorized or manual operated |  |  | motorized |  |
|  | • Motorization |  |  |  |  |
|  | - Rated voltage of the motor |  | Vdc | 220 |  |
|  | • Number of potential free auxiliary contacts |  |  |  |  |
|  | - Closed – Open - Open: COO |  |  | 4 |  |
|  | - Open – Open - Closed: OOC |  |  | 4 |  |
|  | - Open – Closed - Closed: OCC |  |  | 2 |  |
|  | - Open – Closed - Open: OCO |  |  | 2 |  |
|  | • Heating |  |  |  |  |
|  | - Rated voltage |  | Vca | 230 |  |

| TECHNICAL SCHEDULE – Data for Information |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Combinated Disconnector and Earthing - 110kV |  |  |  |  |  |
| Description |  |  | Units | Imposed Values | Guaranteed Values* |
|  | 1. General characteristics |  |  |  |  |
|  | • Place of manufacture |  |  | Specify |  |
|  | • Standards (latest edition) |  |  | IEC 62271-102 |  |
|  | • Single break disconnector |  |  | Yes |  |
|  | • Earthing switch on line side |  |  | Yes |  |
|  | • Earthing switch on CB side |  |  | Yes |  |
|  | • Class |  |  |  |  |
|  | - Main blades |  |  | M1 |  |
|  | - Earth blades |  |  | E1 |  |
|  | 2. Normal service conditions(please refer to the site conditions of each substation) |  |  |  |  |
|  | • Ambient temperature range |  | °C |  |  |
|  | • Relative humidity |  | % |  |  |
|  | • Maximum altitude |  | m |  |  |
|  | • Maximum ice coating |  | mm |  |  |
|  | • Maximum pressure of the wind speed |  | Pa |  |  |
|  | • Solar radiation |  | W/m² |  |  |
|  | 3. Currents Characteristics |  |  |  |  |
|  | • Maximum temperature rise at In (t° ambient: 45°C) |  |  | Specify |  |
|  | 4. Rated voltage and rated insulation level |  |  |  |  |
|  | • Contact resistance |  |  |  |  |
|  | - Main blades |  | μΩ | Specify |  |
|  | - Earth blades |  | μΩ | Specify |  |
|  | 5. Overload conditions |  |  |  |  |
|  | • Permissible overload currents in accordance with the standard IEC 62271-1 |  |  | Yes |  |
|  | 6. Insulators characteritics |  |  |  |  |
|  | • Manufacturer |  |  | Specify |  |
|  | • Type (based IEC) |  |  | Specify |  |
|  | • Used material |  |  | Ceramic |  |
|  | • Profile |  |  | Specify |  |
|  | • Number of elements |  |  | 1 |  |
|  | • Height |  | mm | Specify |  |
|  | • Weight |  | kg | Specify |  |
|  | 7. Disconnector operating device |  |  |  |  |
|  | Main blades |  |  |  |  |
|  | • Type (manufacturer reference) |  |  | Specify |  |
|  | • Motorization |  |  |  |  |
|  | - Rated voltage of the motor |  | Vdc | 220 |  |
|  | - Tolerance |  | % | 85 - 110 |  |
|  | - Capacity |  | W | Specify |  |
|  | - Motor current |  | A | Specify |  |
|  | - Maximum motor current |  | A | Specify |  |
|  | - Rated current for operation at maximum torque |  | A | Specify |  |
|  | - Switching time: |  |  |  |  |
|  | - Closing time of the disconnector |  | s | Specify |  |
|  | - Opening time of the disconnector |  | s | Specify |  |
|  | • Emergency manual operating device available |  |  | Yes |  |
|  | - Type of operating device (crank,….) |  |  | Specify |  |
|  | - Maximal torque needed for manual opening |  | Nm | Specify |  |
|  | - Maximal torque needed for manual closing |  | Nm | Specify |  |
|  | - Maximal operation height above ground level |  | mm | 1500 |  |
|  | • Number of potential free auxiliary contacts |  |  |  |  |
|  | - Closed – Open - Open: COO |  |  | 4 |  |
|  | - Open – Open - Closed: OOC |  |  | 4 |  |
|  | - Open – Closed - Closed: OCC |  |  | 2 |  |
|  | - Open – Closed - Open: OCO |  |  | 2 |  |
|  | - Breaking capacity |  |  | 4 A at 220 V |  |
|  | - Minimum rated current |  |  | 10 A (class 1) |  |
|  | • Heating |  |  |  |  |
|  | - Rated voltage |  | Vca | 230 |  |
|  | - Tolerance |  | % | 85 - 110 |  |
|  | - Power |  | W | Specify |  |
|  | • Protection level |  |  | ≥IP 55 |  |
|  | Earth blades for lines |  |  |  |  |
|  | • Type (manufacturer reference) |  |  | Specify |  |
|  | • Motorization |  |  |  |  |
|  | - Rated voltage of the motor |  | Vdc | 220 |  |
|  | - Tolerance |  | % | 85 - 110 |  |
|  | - Capacity |  | W | Specify |  |
|  | - Motor current |  | A | Specify |  |
|  | - Maximum motor current |  | A | Specify |  |
|  | - Rated current for operation at maximum torque |  | A | Specify |  |
|  | - Switching time: |  |  |  |  |
|  | - Closing time of the earth switch |  | s | Specify |  |
|  | - Opening time of the earth switch |  | s | Specify |  |
|  | • Emergency manual operating device available |  |  | Yes |  |
|  | - Type of operating device (crank,….) |  |  | Specify |  |
|  | - Maximal torque needed for manual opening |  | Nm | Specify |  |
|  | - Maximal torque needed for manual closing |  | Nm | Specify |  |
|  | - Maximal operation height above ground level |  | mm | 1500 |  |
|  | • Number of potential free auxiliary contacts |  |  |  |  |
|  | - Closed – Open - Open: COO |  |  | 4 |  |
|  | - Open – Open - Closed: OOC |  |  | 4 |  |
|  | - Open – Closed - Closed: OCC |  |  | 2 |  |
|  | - Open – Closed - Open: OCO |  |  | 2 |  |
|  | - Breaking capacity |  |  | 4 A at 220 V |  |
|  | - Minimum rated current |  |  | 10 A (class 1) |  |
|  | • Heating |  |  |  |  |
|  | - Rated voltage |  | Vca | 230 |  |
|  | - Tolerance |  | % | 85 - 110 |  |
|  | - Power |  | W | Specify |  |
|  | • Protection level |  |  | ≥IP 55 |  |
|  | Earth blades for Breaker Maintenance and Busbar |  |  |  |  |
|  | • Type of operating device |  |  |  |  |
|  | • Three or single pole operated |  |  | three pole |  |
|  | • Motorized or manual operated |  |  | manual |  |
|  | • Type (manufacturer reference) |  |  | Specify |  |
|  | - Maximal torque needed for manual opening |  | Nm | Specify |  |
|  | - Maximal torque needed for manual closing |  | Nm | Specify |  |
|  | - Maximal operation height above ground level |  | mm | 1500 |  |
|  | • Number of potential free auxiliary contacts |  |  |  |  |
|  | - Closed – Open - Open: COO |  |  | 4 |  |
|  | - Open – Open - Closed: OOC |  |  | 4 |  |
|  | - Breaking capacity |  |  | 4 A at 220 V |  |
|  | - Minimum rated current |  |  | 10 A (class 1) |  |
|  | • Heating |  |  |  |  |
|  | - Rated voltage |  | Vca | 230 |  |
|  | - Tolerance |  | % | 85 - 110 |  |
|  | - Power |  | W | Specify |  |
|  | • Protection level |  |  | ≥IP 55 |  |
|  | Main blades |  |  |  |  |
|  | • Type of operating device |  |  |  |  |
|  | • Three or single pole operated |  |  | three pole |  |
|  | • Motorized or manual operated |  |  | motorized |  |
|  | • Type (manufacturer reference) |  |  | Specify |  |
|  | • Motorization |  |  |  |  |
|  | - Rated voltage of the motor |  | Vdc | 220 |  |
|  | - Tolerance |  | % | 85 - 110 |  |
|  | - Capacity |  | W | Specify |  |
|  | - Motor current |  | A | Specify |  |
|  | - Maximum motor current |  | A | Specify |  |
|  | - Rated current for operation at maximum torque |  | A | Specify |  |
|  | - Switching time: |  |  |  |  |
|  | - Closing time of the disconnector |  | s | Specify |  |
|  | - Opening time of the disconnector |  | s | Specify |  |
|  | • Emergency manual operating device available |  |  | Yes |  |
|  | - Type of operating device (crank,….) |  |  | Specify |  |
|  | - Maximal torque needed for manual opening |  | Nm | Specify |  |
|  | - Maximal torque needed for manual closing |  | Nm | Specify |  |
|  | - Maximal operation height above ground level |  | mm | 1500 |  |
|  | • Number of potential free auxiliary contacts |  |  |  |  |
|  | - Closed – Open - Open: COO |  |  | 4 |  |
|  | - Open – Open - Closed: OOC |  |  | 4 |  |
|  | - Open – Closed - Closed: OCC |  |  | 2 |  |
|  | - Open – Closed - Open: OCO |  |  | 2 |  |
|  | - Breaking capacity |  |  | 4 A at 220 V |  |
|  | - Minimum rated current |  |  | 10 A (class 1) |  |
|  | • Heating |  |  |  |  |
|  | - Rated voltage |  | Vca | 230 |  |
|  | - Tolerance |  | % | 85 - 110 |  |
|  | - Power |  | W | Specify |  |
|  | • Protection level |  |  | ≥IP 55 |  |
|  | 8. Safety and locking |  |  |  |  |
|  | Main blades |  |  |  |  |
|  | • Normal electrical operated mechanism |  |  |  |  |
|  | - Mechanical locking device placed on motor drive |  |  | Yes |  |
|  | - Motor circuit interrupted by the locking device |  |  | Yes |  |
|  | - Padlockable mechanical locking device in open and closed position (padlocking Ø8mm possible) |  |  | Yes |  |
|  | • Manual drive (if applicable) |  |  | N.A. |  |
|  | - Locking coil in combination with push button |  |  | N.A. |  |
|  | - Supply voltage |  | Vdc | N.A. |  |
|  | - Padlockable mechanical locking device in open and closed position (padlocking Ø8mm possible) |  |  | N.A. |  |
|  | Earth blades for lines |  |  |  |  |
|  | • Normal electrical operated mechanism |  |  |  |  |
|  | - Mechanical locking device placed on motor drive |  |  | Yes |  |
|  | - Motor circuit interrupted by the locking device |  |  | Yes |  |
|  | - Padlockable mechanical locking device in open and closed position (padlocking Ø8mm possible) |  |  | Yes |  |
|  | • Manual drive (if applicable) |  |  | N.A. |  |
|  | - Locking coil in combination with push button |  |  | N.A. |  |
|  | - Supply voltage |  | Vdc | N.A. |  |
|  | - Padlockable mechanical locking device in open and closed position (padlocking Ø8mm possible) |  |  | N.A. |  |
|  | Earth blades for Breaker maintenance and Busbar |  |  |  |  |
|  | - Locking coil in combination with push button |  |  | Yes |  |
|  | - Supply voltage |  | Vdc | 220 |  |
|  | - Padlockable mechanical locking device in open and closed position (padlocking Ø8mm possible) |  |  | Yes |  |
|  | Main blades and Earth blades |  |  |  |  |
|  | - Mechanical interlock between main and earth blades |  |  |  |  |
|  | 9. Ergonomics |  |  |  |  |
|  | • Minimum height from ground or circulation level |  |  |  |  |
|  | - bottom skirt of the isolator |  | mm | 2500 |  |
|  | - vertical distance of life part |  | mm | 4500 |  |
|  | • Preferential height from ground or circulation level |  |  |  |  |
|  | - bottom side of the drives |  | mm | 1000 < H < 1600 |  |
|  | - top side of the drives |  | mm | Maximum 2500 |  |
|  | - door handles |  | mm | Maximum 1800 |  |
|  | 10. Mechanical characteristics |  |  |  |  |
|  | • Weight of the complete disconnector |  | kg | Specify |  |
|  | • Weight of the operating mechanisms |  |  |  |  |
|  | - Weight of the main blades operating mechanism |  | kg | Specify |  |
|  | - Weight of the earth blades operating mechanism |  | kg | Specify |  |
|  | 11. Construction details |  |  |  |  |
|  | Main blades |  |  |  |  |
|  | - Used material for contact (Al, electroplated silver or tinned copper) |  |  | Specify |  |
|  | - Contact type |  |  | Specify |  |
|  | - Maximum temperature rise at In (t° ambient: 45°C) |  |  | Specify |  |
|  | - Number of contact fingers |  |  | Specify |  |
|  | - Contact pressure by finger |  | daN | Specify |  |
|  | - Type of electrical connection between elements |  |  | Specify |  |
|  | • HV Terminals |  |  |  |  |
|  | - Diameter (according Inom) |  |  | Specify |  |
|  | - Used material for contact (Al, electroplated silver or tinned copper) |  |  | Specify |  |
|  | - Length |  |  | Specify |  |
|  | - Supply all the parts needed for connecting connection |  |  | Yes |  |
|  | Earth blades |  |  |  |  |
|  | - Used material for contact (Al, electroplated silver or tinned copper) |  |  | Specify |  |
|  | - Contact type |  |  | Specify |  |
|  | - Number of contact fingers |  |  | Specify |  |
|  | - Contact pressure by finger |  | daN | Specify |  |
|  | 12. Paint and corrosion protection |  |  |  |  |
|  | • Oxydable metal parts |  |  | hot dip galvanizing |  |
|  | • Screws, nuts, bolts,…. |  |  |  |  |
|  | - for diameter ≤ M16 stainless steel |  |  | Yes |  |
|  | - for diameter > M16 hot dip galvanized steel and painted |  |  | Yes |  |
|  | • Frame of control panel galvanized |  |  | Yes |  |
|  | • Duplex principle (galvanized + paint) according GTS |  |  | Yes |  |
|  | • Final color paint |  |  |  |  |
|  | - pieces to earth |  |  | Specify |  |
|  | - live parts |  |  | Specify |  |
|  | - insulator's metal flanges |  |  | Specify |  |
|  | - grounded connections, metallic conductors,… free of paint |  |  |  |  |
|  |  |  |  |  |  |
|  | 13. Documents to be submitted |  |  |  |  |
|  | • Submital fase |  |  | 3 ex. |  |
|  | - General documentation |  |  |  |  |
|  | - List of references |  |  |  |  |
|  | - Type test reports |  |  |  |  |
|  | - datasheet completed |  |  |  |  |
|  | - dimensional drawing |  |  |  |  |
|  | • Ordering fase |  |  | 3 ex. |  |
|  | - operating instruction manual |  |  |  |  |
|  | - erection instruction manual |  |  |  |  |
|  | - maintenance instruction manual |  |  |  |  |
|  | - static and dynamic efforts |  |  |  |  |
|  | - drawings |  |  |  |  |
|  | - detailed dimensional drawing with an indication of weight and efforts |  |  |  |  |
|  | - drawing of the operating cubicles |  |  |  |  |
|  | - drawing of the rating plate |  |  |  |  |
|  | - LV diagrams |  |  |  |  |
|  | - drawing of electrical circuits |  |  |  |  |
|  | - principle diagram of the operating mechanism for main blades |  |  |  |  |
|  | - principle diagram of the operating mechanism for earth blades |  |  |  |  |
|  | • Completed Manufactuer final report including |  |  | 3 ex. |  |
|  | - operating instruction manual |  |  |  |  |
|  | - erection instruction manual |  |  |  |  |
|  | - maintenance instruction manual |  |  |  |  |
|  | - as built drawings and schematics |  |  |  |  |
|  | - factory test report |  |  |  |  |
|  | 14. Languages |  |  |  |  |
|  | • All documents establish in English |  |  | Yes |  |

| TECHNICAL SCHEDULE – Main Data |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Earthing Disconnector Switch - 110kV |  |  |  |  |  |
| Description |  |  | Units | Imposed Values | Guaranteed Values* |
|  | 1. General characteristics |  |  |  |  |
|  | • Manufacturer |  |  | Specify |  |
|  | • Type |  |  | Specify |  |
|  | • Number of poles |  |  | 1 |  |
|  | • Indoor/Outdoor installation |  |  | Outdoor |  |
|  | • Maximum opening time |  | s | 10 |  |
|  | • Maximum closing time |  | s | 10 |  |
|  | • Number of switching events until the first maintenance |  |  | 1000 |  |
|  | • Insulator type |  |  | Brown Porcelain |  |
|  | • Minimum nominal creeping distance |  | mm / kV | 31 |  |
|  | 2. Normal service conditions |  |  |  |  |
|  | • Ambient temperature range |  | °C | -35 to +50 |  |
|  | 3. Rated withstand currents |  |  |  |  |
|  | • Rated short time withstand current |  | kA | 40 |  |
|  | • Rated peak withstand current |  | kA peak | 100 |  |
|  | • Rated duration of short circuit |  | s | 3 |  |
|  | 4. Rated voltage and rated insulation level |  |  |  |  |
|  | • Network nominal voltage |  | kV | 110 |  |
|  | • Rated voltage for equipment |  | kV | 126 |  |
|  | • Rated power frequency withstand voltage 50Hz - 1 min (Ud) |  |  |  |  |
|  | - Phase to earth |  | kV | 230 |  |
|  | - Across open switching device |  | kV | 265 |  |
|  | • Rated lightning impulse withstand voltage (1,2/50µs) (Up) |  |  |  |  |
|  | - Phase to earth |  | kV peak | 550 |  |
|  | - Across open switching device |  | kV peak | 630 |  |
|  | 6. Operating device |  |  |  |  |
|  | • Type of operating mechanism |  |  |  |  |
|  | - Single or three pole operated |  |  | single pole |  |
|  | - motorized or manual operated |  |  | manual |  |
|  | • Number of potential free auxiliary contacts |  |  |  |  |
|  | - Close - Open - Open: COO |  |  | 4 |  |
|  | - Open - Open - Close: OOC |  |  | 4 |  |
|  | • Heating |  |  |  |  |
|  | - Rated voltage (50Hz) |  | Vca | 230 |  |

| TECHNICAL SCHEDULE – Data for Information |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Earthing Disconnector Switch - 110kV |  |  |  |  |  |
| Description |  |  | Units | Imposed Values | Guaranteed Values* |
|  | 1. General characteristics |  |  |  |  |
|  | •Place of manufacture |  |  | Specify |  |
|  | • Standards (latest edition) |  |  | IEC 62271-203 |  |
|  | • Class |  |  |  |  |
|  | - Earthing blades |  |  | E1 |  |
|  | 2. Normal service conditions(please refer to the site conditions of each substation) |  |  |  |  |
|  | • Ambient temperature range |  | °C |  |  |
|  | • Relative humidity |  | % |  |  |
|  | • Maximum altitude |  | m |  |  |
|  | • Maximum ice coating |  | mm |  |  |
|  | • Maximum pressure of the wind speed |  | Pa |  |  |
|  | • Solar radiation |  | W/m² |  |  |
|  | 4. Rated voltage and rated insulation level |  |  |  |  |
|  | • Contact resistance |  | μΩ | Specify |  |
|  | 5. Insulators |  |  |  |  |
|  | • Manufacturer |  |  | Specify |  |
|  | • Type (based IEC) |  |  | Specify |  |
|  | • Used material |  |  | Ceramic |  |
|  | • Height |  | mm | Specify |  |
|  | • Weight |  | kg | Specify |  |
|  | • Number of elements |  |  | 1 |  |
|  | • Profile |  |  | Specify |  |
|  | 6. Operating device |  |  |  |  |
|  | • Type of operating mechanism |  |  |  |  |
|  | - Single or three pole operated |  |  | single pole |  |
|  | - motorized or manual operated |  |  | manual |  |
|  | - type (manufacturer's reference) |  |  | Specify |  |
|  | • Manual operated mechanism |  |  |  |  |
|  | - Maximal torque needed for manual opening |  | Nm | Specify |  |
|  | - Maximal torque needed for manual closing |  | Nm | Specify |  |
|  | - Maximal operation height above ground level |  | mm | 1500 |  |
|  | • Class |  |  |  |  |
|  | - Earthing blades |  |  | E1 |  |
|  | • Three position auxiliary contact according IEC 60129 |  |  |  |  |
|  | - Number of potential free auxiliary contacts |  |  |  |  |
|  | - Close - Open - Open: COO |  |  | 4 |  |
|  | - Open - Open - Close: OOC |  |  | 4 |  |
|  | - Breaking capacity |  |  | 4 A at 220 V |  |
|  | - Minimum rated current |  |  | 10 A (class 1) |  |
|  | • Heating |  |  |  |  |
|  | - Rated voltage (50Hz) |  | Vca | 230 |  |
|  | - Tolerances |  | % | 85 to 110 |  |
|  | - Rated power |  | W | Specify |  |
|  | • Protection level IP |  |  | IP 55 |  |
|  | 7. Safety and locking |  |  |  |  |
|  | • Locking coil in combination with push button |  |  | Yes |  |
|  | • Supply voltage |  | Vdc | 220 |  |
|  | • Padlockable mechanical locking device in open and closed position (padlocking Ø8mm possible) |  |  | Yes |  |
|  | 8. Ergonomics |  |  |  |  |
|  | • Minimum height from ground or circulation level |  |  |  |  |
|  | - bottom skirt of the isolator |  | mm | 2500 |  |
|  | - vertical distance of life part |  | mm | 4700 |  |
|  | • Preferential height from ground or circulation level |  |  |  |  |
|  | - bottom side of the drives |  | mm | 1000 < H < 1600 |  |
|  | - top side of the drives |  | mm | Maximum 2500 |  |
|  | - door handles |  | mm | Maximum 1800 |  |
|  | 9. Mechanical characteristics |  |  |  |  |
|  | • Weight of the complete earthing switch |  | kg | Specify |  |
|  | • Weight of the manual mechanism |  | kg | Specify |  |
|  | 10. Construction details |  |  |  |  |
|  | • Used material for contact (Al, electroplated silver or tinned copper, others) |  |  | Specify |  |
|  | • Contact type |  |  | Specify |  |
|  | • Number of contact fingers |  |  | Specify |  |
|  | • Contact pressure by finger |  |  | Specify |  |
|  | 11. Paint and corrosion protection |  |  |  |  |
|  | • Oxydable metal parts |  |  | hot dip galvanizing |  |
|  | • Screws, nuts, bolts,…. |  |  |  |  |
|  | - for diameter ≤ M16 stainless steel |  |  | Yes |  |
|  | - for diameter > M16 hot dip galvanized steel and painted |  |  | Yes |  |
|  | • Frame of control panel galvanized |  |  | Yes |  |
|  | • Duplex principle (galvanized + paint) according GTS |  |  | Yes |  |
|  | • Final color paint |  |  |  |  |
|  | - pieces to earth |  |  | Specify |  |
|  | - live parts |  |  | Specify |  |
|  | - insulator's metal flanges |  |  | Specify |  |
|  | - grounded connections, metallic conductors,… free of paint |  |  |  |  |
|  | 12. Documents to be submitted |  |  |  |  |
|  | • Submital fase |  |  | 3 ex. |  |
|  | - General documentation |  |  |  |  |
|  | - List of references |  |  |  |  |
|  | - Type test reports |  |  |  |  |
|  | - datasheet completed |  |  |  |  |
|  | - dimensional drawing |  |  |  |  |
|  | • Ordering fase |  |  | 3 ex. |  |
|  | - operating instruction manual |  |  |  |  |
|  | - erection instruction manual |  |  |  |  |
|  | - maintenance instruction manual |  |  |  |  |
|  | - static and dynamic efforts |  |  |  |  |
|  | - drawings |  |  |  |  |
|  | - detailed dimensional drawing with an indication of weight and efforts |  |  |  |  |
|  | - drawing of the operating cubicle |  |  |  |  |
|  | - drawing of the rating plate |  |  |  |  |
|  | - LV diagrams |  |  |  |  |
|  | - drawing of electrical circuits |  |  |  |  |
|  | - principle diagram of the operating mechanism |  |  |  |  |
|  | • Completed Manufactuer final report including |  |  | 3 ex. |  |
|  | - operating instruction manual |  |  |  |  |
|  | - erection instruction manual |  |  |  |  |
|  | - maintenance instruction manual |  |  |  |  |
|  | - as built drawings and schematics |  |  |  |  |
|  | - factory test report |  |  |  |  |
|  | 13. Languages |  |  |  |  |
|  | • All documents establish in English |  |  | Yes |  |

| TECHNICAL SCHEDULE – Main Data |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Insulating Support - 110kV |  |  |  |  |  |
| Description |  |  | Units | Imposed Values | Guaranteed Values |
|  | 1. General characteristics |  |  |  |  |
|  | • Manufacturer |  |  | Specify |  |
|  | • Type |  |  | Specify |  |
|  | • Installation |  |  | Outdoor |  |
|  | • Rated frequency (fr) |  | Hz | 50 |  |
|  | 2. Normal service conditions |  |  |  |  |
|  | • Ambient temperature range |  | °C | -35 to +50 |  |
|  | 3. Electrical characteristics |  |  |  |  |
|  | • Network nominal voltage |  | kV | 110 |  |
|  | • Maximum service voltage (Um) |  | kV | 126 |  |
|  | - Power frequency withstand voltage 50Hz - 1 min.(Ud) |  | kV | 230 |  |
|  | - Lightning Impulse withstand voltage (1,2/50µs) |  | kV | 550 |  |
|  | 4. Characteristics of insulating support |  |  |  |  |
|  | • Housing (porcelain, polymer) |  |  | Porcelain - Brown |  |
|  | • Minimum phase creepage distance |  | mm/kV | 31 |  |

| TECHNICAL SCHEDULE – Data for Information |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Insulating Support - 110kV |  |  |  |  |  |
| Description |  |  | Units | Imposed Values | Guaranteed Values |
|  | 1. General characteristics |  |  |  |  |
|  | •Place of manufacture |  |  | Specify |  |
|  | • Standards |  |  | IEC 60273 |  |
|  | • Rated voltage (Ur) |  | kV | 123 |  |
|  | 2. Normal service conditions(please refer to the site conditions of each substation) |  |  |  |  |
|  | • Ambient temperature range |  | °C |  |  |
|  | • Relative humidity |  | % |  |  |
|  | • Maximum altitude |  | m |  |  |
|  | • Maximum ice coating |  | mm |  |  |
|  | • Maximum pressure of the wind speed |  | Pa |  |  |
|  | • Solar radiation |  | W/m² |  |  |
|  | 3. Mechanical characteristics |  |  |  |  |
|  | • Flexion |  |  |  |  |
|  | -breaking load |  | N | Specify |  |
|  | -permissible continuous effort on top without damage |  | % | Specify |  |
|  | -permissible effort on top on short circuit without damage |  | % | Specify |  |
|  | -duration |  | s | Specify |  |
|  | • Torsion: breaking load |  | Nm | Specify |  |
|  | • Strength: breaking load |  | N | Specify |  |
|  | • Compression: breaking load |  | N | Specify |  |
|  | 4. Characteristics of insulating support |  |  |  |  |
|  | • Mounting |  |  | standing or hanging |  |
|  | • Number of elementary columns |  |  | Specify |  |
|  | • Total height of the insulating support |  | mm | Specify |  |
|  | • Fixations |  |  |  |  |
|  | -top (voltage side) |  |  |  |  |
|  | -circle diameter of fixation |  | mm | Specify |  |
|  | -number of screws |  |  | Specify |  |
|  | -drillings for screws |  |  | Specify |  |
|  | -base (earth side) |  |  |  |  |
|  | -circle diameter of fixation |  | mm | Specify |  |
|  | -number of screws |  |  | Specify |  |
|  | -drillings for screws |  |  | Specify |  |
|  | • Weight |  | kg | Specify |  |
|  | 5. Paint and corrosion protection |  |  |  |  |
|  | • Oxydable metal parts |  |  | hot dip galvanizing |  |
|  | • Screws, nuts, bolts,…. |  |  |  |  |
|  | - for diameter ≤ M16 stainless steel |  |  | Yes |  |
|  | - for diameter > M16 hot dip galvanized steel and painted |  |  | Yes |  |
|  | • Duplex principle (galvanized + paint) according GTS |  |  | Yes |  |
|  | • Final color paint |  |  |  |  |
|  | - pieces to earth |  |  | Specify |  |
|  | - live parts |  |  | Specify |  |
|  | - insulator's metal flanges |  |  | Specify |  |
|  | - grounded connections, metallic conductors,… free of paint |  |  |  |  |
|  |  |  |  |  |  |
|  | 6. Documents to be submitted |  |  |  |  |
|  | • Submital fase |  |  | 3 ex. |  |
|  | - General documentation |  |  |  |  |
|  | - datasheet completed |  |  |  |  |
|  | - dimensional drawing |  |  |  |  |
|  | • Ordering fase |  |  | 3 ex. |  |
|  | - erection instruction manual |  |  |  |  |
|  | - maintenance instruction manual |  |  |  |  |
|  | - static and dynamic efforts |  |  |  |  |
|  | - dimensional drawing |  |  |  |  |
|  | • Completed Manufactuer final report including |  |  | 3 ex. |  |
|  | - erection instruction manual |  |  |  |  |
|  | - maintenance instruction manual |  |  |  |  |
|  | - as built drawing |  |  |  |  |
|  | 7. Languages |  |  |  |  |
|  | • All documents establish in English |  |  | Yes |  |

| TECHNICAL SCHEDULE – Main Data |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Phase Surge Arrester - 110kV |  |  |  |  |  |
| Description |  |  | Units | Imposed Values | Guaranteed Values |
|  | 1. General characteristics |  |  |  |  |
|  | • Manufacturer |  |  | Specify |  |
|  | • Type |  |  | Specify |  |
|  | • Installation |  |  | Outdoor |  |
|  | • Housing (porcelain, polymer) |  |  | Porcelain – Brown |  |
|  | • Minimum phase creepage distance |  | mm/kV | 31 |  |
|  | 2. Normal service conditions |  |  |  |  |
|  | • Ambient temperature range |  | °C | -35 to +50 |  |
|  | 3. Electrical characteristics |  |  |  |  |
|  | • Rated frequency (fr) |  | Hz | 50 |  |
|  | • Network nominal voltage |  | kV | 110 |  |
|  | • Maximum service voltage (Um) |  | kV | 126 |  |
|  | • Nominal discharge current |  | kA peak | 10 |  |
|  | • Continuous Operating Voltage (Uc - COV) |  | kV | 76 |  |
|  | • Insulation level for the housing |  |  |  |  |
|  | - Power frequency withstand voltage 50Hz - 1 min. |  | kV | 230 |  |
|  | - Lightning Impulse withstand voltage (1,2/50µs) |  | kV | 550 |  |

| TECHNICAL SCHEDULE – Data for Information |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Phase Surge Arrester - 110kV |  |  |  |  |  |
| Description |  |  | Units | Imposed Values | Guaranteed Values |
|  | 1. General characteristics |  |  |  |  |
|  | •Place of manufacture |  |  | Specify |  |
|  | • Standards |  |  | IEC |  |
|  | • Construction type |  |  | MO (metal oxide) |  |
|  | • Model |  |  | Specify |  |
|  | • Surge counter |  |  | Yes |  |
|  | -number |  |  | 1 by phase |  |
|  | -type |  |  | Specify |  |
|  | 2. Normal service conditions(please refer to the site conditions of each substation) |  |  |  |  |
|  | • Ambient temperature range |  | °C |  |  |
|  | • Relative humidity |  | % |  |  |
|  | • Maximum altitude |  | m |  |  |
|  | • Maximum ice coating |  | mm |  |  |
|  | • Maximum pressure of the wind speed |  | Pa |  |  |
|  | • Solar radiation |  | W/m² |  |  |
|  | 3. Electrical characteristics |  |  |  |  |
|  | • Surge arrester rated voltage (Ur) |  | kV | Specify |  |
|  | • Maximum temporary Over Voltage |  |  |  |  |
|  | - for 1 s |  | kV | Specify |  |
|  | - for 10 s |  | kV | Specify |  |
|  | • Maximum residual voltages for a lightning impulse 8/20 μs |  |  |  |  |
|  | - at I = 5 kA |  | kV peak | Specify |  |
|  | - at I = 10 kA |  | kV peak | Specify |  |
|  | - at I = 20 kA |  | kV peak | Specify |  |
|  | • Maximum residual voltages for a lightning impulse 30/... μs |  |  |  |  |
|  | - at I = 1 kA |  | kV peak | Specify |  |
|  | • Line discharge class (IEC 60099-4) |  |  | Specify |  |
|  | • Reference current and voltage |  | kV /mA | Specify |  |
|  | 4. Mechanical characteristics |  |  |  |  |
|  | • Pollution Class |  |  | outstanding no pollution) |  |
|  | • Over-pressure valve |  |  | Yes/No |  |
|  | - type |  |  | Specify |  |
|  | - pressure relief capability |  | kA | ≥25 |  |
|  | • Maximum allowed strength (MPSL) |  | N | Specify |  |
|  | • Maximum dynamic allowed strength (MPDSL) |  | N | Specify |  |
|  | • Total height (including insulated base) |  | mm | Specify |  |
|  | • Total weight |  | kg | Specify |  |
|  | 5. Contruction details |  |  |  |  |
|  | • Type of line connection (Al, ...) |  |  | Specify |  |
|  | • Type of ground connection ( stainless steel, ….) |  |  | Specify |  |
|  | • Insulated base |  |  | Yes |  |
|  | • Guard ring (outer diameter) |  | mm | Specify |  |
|  | • Number of elementary columns |  |  | Specify |  |
|  | • Terminal for connection of online Leakage Current Measurement system |  |  | Yes |  |
|  | 6. Paint and corrosion protection |  |  |  |  |
|  | • Oxydable metal parts |  |  | hot dip galvanizing |  |
|  | • Screws, nuts, bolts,…. |  |  |  |  |
|  | - for diameter ≤ M16 stainless steel |  |  | Yes |  |
|  | - for diameter > M16 hot dip galvanized steel and painted |  |  | Yes |  |
|  | • Duplex principle (galvanized + paint) according GTS |  |  | Yes |  |
|  | • Final color paint |  |  |  |  |
|  | - pieces to earth |  |  | Specify |  |
|  | - live parts |  |  | Specify |  |
|  |  |  |  |  |  |
|  | 7. Testing |  |  |  |  |
|  | • Reports of type tests on similar equipment |  |  | Yes |  |
|  | • Routine test according to IEC 60099.4 |  |  | Yes |  |
|  | 8. Documents to be submitted |  |  |  |  |
|  | • Submital fase |  |  | 3 ex. |  |
|  | - General documentation |  |  |  |  |
|  | - List of references |  |  |  |  |
|  | - Type test reports |  |  |  |  |
|  | - datasheet completed |  |  |  |  |
|  | - dimensional drawing |  |  |  |  |
|  | • Ordering fase |  |  | 3 ex. |  |
|  | - erection instruction manual |  |  |  |  |
|  | - maintenance instruction manual |  |  |  |  |
|  | - static and dynamic efforts |  |  |  |  |
|  | - voltage curve at power-frequency in function of time |  |  |  |  |
|  | - drawings |  |  |  |  |
|  | - detailed dimensional drawing |  |  |  |  |
|  | - drawing of the rating plate |  |  |  |  |
|  | • Completed Manufactuer final report including |  |  | 3 ex. |  |
|  | - erection instruction manual |  |  |  |  |
|  | - maintenance instruction manual |  |  |  |  |
|  | - as built drawings |  |  |  |  |
|  | - voltage curve at power-frequency in function of time |  |  |  |  |
|  | - factory test report |  |  |  |  |
|  | 9. Languages |  |  |  |  |
|  | • All documents establish in English |  |  | Yes |  |

TECHNICAL SCHEDULE – Main Data Capacitive Voltage Transformer 110kV. Description; Units; Imposed Values; Guaranteed Values. 1. General characteristics. • Manufacturer; Specify. • Type; Single phase Oil Immersed Capacitive. • Indoor/Outdoor installation; Outdoor. • Insulator type; Brown Procelain. • Minimum nominal creeping distance; mm / kV; 31. 2. Normal service conditions. • Ambient temperature range; °C; -35 to +50. 3. Electrical characteristics. • Service voltage; kV; 110. • Rated frequency (fr); Hz; 50. • Rated voltage (Ur); kV; 126. • Rated short duration power-frequency withstand voltage (AC) 1min-50Hz (Ud); kV; 230. • Rated lightning impulse withstand voltage (Up); kV peak; 550. 4. Windings characteristics. • Rated primary voltage; kV eff; 110/√3. • Voltage factors. - 1.2 Un - permanent; Yes. - 1.9 Un - 8 hours; Yes. • Secondary windings. - number; 3. • Rated secondary voltage. - Winding nr.1 (metering); V; 100/√3. - Winding nr.2 (measuring); V; 100/√3. - Winding nr.3 (ptotection); V; 100/√3. • Accuracy class. - Winding nr.1 (metering); cl.; 0.2. - Winding nr.2 (measuring); cl.; 0.5. - Winding nr.3 (ptotection); cl.; 3P. • Accuracy burden. - Winding nr.1 (metering); VA; 50. - Winding nr.2 (measuring); VA; 200. - Winding nr.3 (ptotection); VA; 200. • Temperature rise limit (secondary); VA; Specify. • Secondary windings. - Short duration power-frequency withstand voltage (AC) 1min-50Hz; kV; 3. • Rated frequency range (% fr). - cl.0.2; %; 99 to 101. - cl.0.5; %; 99 to 101. - 3P; %; 96 to 102. TECHNICAL SCHEDULE – Data for Information Capacitive Voltage Transformer 110Kv. Description; Units; Imposed Values; Guaranteed Values. 1. General characteristics. • Place of manufacture; Specify. • Type; Specify. • Standards (latest edition); IEC 61869-1/5 IEC 60358-1/2. • Planned for line trap mounting; Yes. • High frequency output terminal for HF signal transmission; Yes. • Completely sealed construction; Specify. • Hermeticity type system; Specify. 2. Normal service conditions(please refer to the site conditions of each substation). • Ambient temperature range; °C. • Relative humidity; %. • Maximum altitude; m. • Maximum ice coating; mm. • Maximum pressure of the wind speed; Pa. • Solar radiation; W/m². 3. Capacitors Values. • Capacity of the HV capacitor (upper) capacitor C1; pF; Specify. • Capacity of intermediate capacitor (lower) C2; pF; Specify. CN=C1.C2C1+C2 • Rated Capacity.; pF; à spécifier. • Tolerances on rated capacity; %; -5 à 10. 4. Capacitors characteristics.. • Tangent δ or loss angle of the capacitor. - at 20°C and 50Hz, between 0.1 and 1.5 x Ur,p (225/√3kV); < 0.005. - maximum variation at Ur,p (225/√3kV) and between +5°C and 50°C after 12 months in service; ≤ 0.001. • maximum temperature coefficient of the capacitor; % / °C; < 0.1. • capacitors stability coefficient (after 12 months in service); %; 1. • Capacitor voltage gradient at Ur/√3; kV/mm; Specify. 5. Additional conditions for HF signal transmission. • Apparent capacity for frequencies between 40 to 400kHz; pF; 5000. - maximum variations; %; -12% / 20%. - parasitic capacitance of the LV terminal; pF; < 500. - parasitic conductance of the LV terminal; µS; < 50. - equivalent series resistance for frequencies between 40 to 400kHz; Ω; < 40. 6. Insulation characteritics. Capacitive units; Specify. • Internal insulation; Specify. • Oil. - type; Specify. - supplier and oil reference; Specify. Electromagnetic unit; Specify. • Internal insulation; Specify. • Oil. - type; Specify. - supplier and oil reference; Specify. External insulation. • Manufacturer; Specify. • Number of elements; 1. 7. Mechanical characteristics. • Total height; mm; Specify. • Total weight; kg; Specify. • Primary terminals. - alloy; Tinned copper. - diameter; mm; Specify. - Contact length; mm; Specify. - Height (axis ground surface - primary terminal); mm; Specify. • Capacitive units. - total weight; kg; Specify. - oil weight; kg; Specify. • Electromagnetic unit. - total weight; kg; Specify. - oil weight; kg; Specify. • Transportation weight. - Capacitor C1; kg; Specify. - Capacitor C2; kg; Specify. 8. Paint and corrosion protection. • Oxydable metal parts; hot dip galvanizing. • Screws, nuts, bolts,….. - for diameter ≤ M16 stainless steel; Yes. - for diameter > M16 hot dip galvanized steel and painted; Yes. • Frame of control panel galvanized; Yes. • Duplex principle (galvanized + paint) according GTS; Yes. • Final color paint. - pieces to earth; Specify. - live parts; Specify. - insulator's metal flanges; Specify. - grounded connections, metallic conductors,… free of paint. ; . 9. Documents to be submitted. • Submital fase; 3 ex.. - General documentation. - List of references. - Type test reports. - datasheet completed. - dimensional drawing. • Ordering fase; 3 ex.. - erection instruction manual. - maintenance instruction manual. - static and dynamic efforts. - detailed description of the air-oil hermeticity system. - drawings. - detailed dimensional drawing. - dimensional drawing of the Capacitors. - dimensional drawing of the electromagnetic unit. - drawing of the LV terminals cabinet. - drawing of the rating plate. • Completed Manufactuer final report including; 3 ex.. - erection instruction manual. - maintenance instruction manual. - as built drawings and schematics. - factory test report. 10. Languages. • All documents establish in English; Yes.

| TECHNICAL SCHEDULE – Main Data Three phase Circuit Breaker – 220 kV – Single pole operated |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Description |  |  | Units | Imposed Values | Guaranteed Values* |
|  | 1. General characteristics |  |  |  |  |
|  | • Manufacturer |  |  | Specify |  |
|  | • Type |  |  | Specify |  |
|  | • Number of poles |  |  | 3 |  |
|  | • Indoor/Outdoor installation |  |  | Outdoor |  |
|  | • Quenching fluid |  |  | SF6 |  |
|  | • Network nominal voltage (Un) |  | kV | 220 |  |
|  | • Highest Operating voltage (UM) |  | kV | 252 |  |
|  | • Rated frequency (fr) |  | Hz | 50 |  |
|  | • Number of breaking chamber per pole |  |  | 1 |  |
|  | • Action of CB operating mechanism |  |  | Single pole |  |
|  | • Insulator |  |  | Brown Porcelain |  |
|  | • Minimum phase creepage distance |  | mm/kV | 31 |  |
|  | 2. Circuit breaker class |  |  |  |  |
|  | • minimum number of operations |  |  | 10 000 |  |
|  | • minimum number of operations at rated current before first maintenance |  |  | 3000 |  |
|  | • minimum number of operations at rated short-circuit current for each phase before first maintenance |  |  | 12 |  |
|  | • Percent of yearly gas leakage |  | % | ≤ 0,3 |  |
|  | 3. Normal service conditions |  |  |  |  |
|  | • Ambient temperature range |  | °C | -35 to +50 |  |
|  | 4. Rated withstand currents |  |  |  |  |
|  | • Rated bay current |  | A | 1600 |  |
|  | • Rated short time withstand current |  | kA | 40 |  |
|  | • Rated peak withstand current |  | kA peak | 100 |  |
|  | • Rated duration of short circuit |  | s | 3 |  |
|  | 5. Rated voltage and rated insulation level |  |  |  |  |
|  | • Rated voltage for equipment (Ur) |  | kV | 245 |  |
|  | • Rated short duration power-frequency withstand voltage (AC) 1min-50Hz |  |  |  |  |
|  | - Between phases, phase to earth |  | kV | 460 |  |
|  | - Across open switching device |  | kV | 460 |  |
|  | • Rated lightning impulse withstand voltage (1,2/50µs) (Up) |  |  |  |  |
|  | - Between phases, phase to earth |  | kV peak | 1050 |  |
|  | - Across open switching device |  | kV peak | 1050 |  |
|  | 6. Tripping and closing characteristics |  |  |  |  |
|  | • Rated short circuit breaking current |  |  |  |  |
|  | - time constant of the asymmetric component (dc) of the rated short circuit current |  | ms | 45 |  |
|  | • Fault at the HV terminals of the CB - rated transient recovery voltage with |  |  |  |  |
|  | - first-pole-to-clear-factor |  |  | 1,3 |  |
|  | 7. Operation durations |  |  |  |  |
|  | • Maximum closing time |  | ms | < 150 |  |
|  | • Maximum breaking time |  | ms | < 40 |  |
|  | • After a complete operating sequence O-0,3s-CO- 3min-CO, the operating mechanism should have enough energy left to proceed one more CO cycle within |  | s | Specify |  |
|  | 8. Technical characteristics of the auxiliary circuits |  |  |  |  |
|  | • Operating voltage of the closing circuits |  |  |  |  |
|  | - voltage |  | Vdc | 220 |  |
|  | - operating range |  | % | 85 to 110 |  |
|  | • Operating voltage of the tripping coils |  |  |  |  |
|  | - voltage |  | Vdc | 220 |  |
|  | - operating range |  | % | 70 to 110 |  |
|  | • Operating voltage of the motor |  |  |  |  |
|  | - voltage |  | Vdc | 220 |  |
|  | - operating range |  | % | 85 to 110 |  |
|  | • Voltage of the heating circuits |  | Vac | 230 |  |
|  | 9. Operating mechanism of the CB |  |  |  |  |
|  | • Single pole operated |  |  | Single pole + CCC |  |
|  | • Type (energy) |  |  | Spring |  |
|  | • Number of closing coils |  |  | 2 |  |
|  | • Number of trip coils |  |  | 2 |  |
|  | - number of free of potential open contacts (NO) |  |  | min. 5, specify |  |
|  | - number of free of potential close contacts (NC) |  |  | min. 5, specify |  |

| TECHNICAL SCHEDULE – Data for Information Three phase Circuit Breaker – 220 kV – Single pole operated |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Description |  |  | Units | Imposed Values | Guaranteed Values* |
|  | 1. General characteristics |  |  |  |  |
|  | • Place of manufacture |  |  | Specify |  |
|  | • Standards (latest edition) |  |  | IEC 62271-100 IEC 62271-1 |  |
|  | • First-pole-to-clear-factor |  |  | 1.3 |  |
|  | • Rated operating sequence O-0,3s-CO-3min-CO |  |  | Yes |  |
|  | • Number of grading capacitor per pole |  |  | N.A. |  |
|  | • Action of CB operating mechanism |  |  | Single pole |  |
|  | 2. Circuit breaker class |  |  |  |  |
|  | • CB mechanicam life classidication |  |  | M1 |  |
|  | • CB electrical life classiffication |  |  | E1 |  |
|  | • CB restrike probability classification |  |  | C1 |  |
|  | 3. Normal service conditions(please refer to the site conditions of each substation) |  |  |  |  |
|  | • Ambient temperature range |  | °C |  |  |
|  | • Relative humidity |  | % |  |  |
|  | • Maximum altitude |  | m |  |  |
|  | • Maximum ice coating |  | mm |  |  |
|  | • Maximum pressure of the wind speed |  | Pa |  |  |
|  | • Solar radiation |  | W/m² |  |  |
|  | 4. Overload capabilities |  |  |  |  |
|  | • Permissible overload currents in accordance with the standard IEC 62271-1 |  |  | Yes |  |
|  | 5. Rated voltage and rated insulation level |  |  |  |  |
|  | • Radio disturbance voltage at 1.1 U / -1MHz |  | μV | ≤ 2500 max. |  |
|  | 6. Tripping and closing characteristics |  |  |  |  |
|  | • Rated short circuit breaking current |  |  |  |  |
|  | - minimum opening time (m.o.t) |  | ms | Specify |  |
|  | - percentage of the asymmetric component ( at 10 ms + m.o.t) |  | % | Specify |  |
|  | - total I |  | kA | Specify |  |
|  | • Fault at the HV terminals of the CB - rated transient recovery voltage with |  |  |  |  |
|  | - rate of rise of recovery voltage (RRRV) |  | kV/µs | 2 |  |
|  | - transient recovery voltage peak value |  | kV | 364 |  |
|  | • Rated peak short circuit making current |  | kA peak | 100 |  |
|  | • On HV line, close fault occuring - rated transient recovery voltage |  |  |  |  |
|  | - fault on line side |  |  |  |  |
|  | . full wave impedance |  | Ω | 450 |  |
|  | . rate of rise factor of the recovery voltage |  | kV/μs.kA | 0,2 |  |
|  | . rated peak factor |  |  | 1,6 |  |
|  | - fault at source side (according IEC 56, table IV) |  |  |  |  |
|  | . rate of rise of recovery voltage |  | kV/µs | 2 |  |
|  | . peak value of the transient recovery voltage |  | kV | 280 |  |
|  | • Rated out-of-phase breaking current in discripency with a rated recovery voltage 2 x U /. |  | kA | 7.875 |  |
|  | • Rated line-charging breaking current (no load) |  |  |  |  |
|  | - rated short-circuit breaking current |  | A | 125. |  |
|  | - maximum overvoltage guarented without arcing |  | kV peak | < 2.5 x 245 |  |
|  | • Rated cable-charging breaking current no load) |  |  |  |  |
|  | - rated short-circuit breaking current |  | A | 250. |  |
|  | - maximum overvoltage guarented without arcing |  | kV peak | < 2.5 x 245 |  |
|  | • Rated maximum capacitive breaking current |  |  |  |  |
|  | - rated short-circuit breaking current |  | A | 400. |  |
|  | - maximum overvoltage guarented without arcing |  | kV peak | < 2.5 x 245 |  |
|  | • Rated small inductive breaking current |  |  |  |  |
|  | - rated short-circuit breaking current |  | A | Specify. |  |
|  | - maximum overvoltage guarented without arcing |  | kV peak | < 2.5 x 245 |  |
|  | • Number of operations taking into account the maintenance program specified by the manufacturer |  |  | min.2000 (class M1) |  |
|  | 7. Operation durations |  |  |  |  |
|  | • Maximum opening time |  | ms | Specify |  |
|  | • Maximum dead time (between break and restore) |  | ms | Specify |  |
|  | • Maximum discrepancy between |  |  |  |  |
|  | - the breaking chamber of a same pole |  |  |  |  |
|  | . during closing operation |  | ms | N.A. |  |
|  | . during opening operation |  | ms | N.A. |  |
|  | - the poles of different phases |  |  |  |  |
|  | . during closing operation |  | ms | 5 |  |
|  | . during opening operation |  | ms | 3.33 |  |
|  | • Minimal duration of the switching impuls for |  |  |  |  |
|  | - closing coil |  | ms | Specify |  |
|  | - trip coil |  | ms | Specify |  |
|  | 8. Technical characteristics of the auxiliary circuits |  |  |  |  |
|  | • Power consumption |  |  |  |  |
|  | - closing coil |  | W | Specify |  |
|  | - tripping coil |  | W | Specify |  |
|  | - motor of the operating mechanism |  | W | Specify |  |
|  | - continuous heating |  | W | Specify |  |
|  | - heating with thermostat |  | W | Specify |  |
|  | 9. Breaking chamber |  |  |  |  |
|  | • Quenching fluid |  |  | SF6 |  |
|  | - Filling in pressure |  | MPa (abs) | Specify |  |
|  | - first alarm pressure |  | MPa (abs) | Specify |  |
|  | - second alarm pressur (lockout or trip) |  | MPa (abs) | Specify |  |
|  | • Number of breaking chamber per poles of the CB |  |  | 1 |  |
|  | • Rated value of the grading capacitor |  | pF | N.A. |  |
|  | • Gas quantity per pole of the CB |  | kg | Specify |  |
|  | • Total course of the moving contact in one breaking chamber |  | mm | Specify |  |
|  | • Distance between the mains contact in one breaking chamber |  | mm | Specify |  |
|  | • Operating speed of the moving contact |  |  |  |  |
|  | - closing time |  | m/s | Specify |  |
|  | - breaking time |  | m/s | Specify |  |
|  | • Densimeter of temperature compensated manometer (SF6 monitoring) |  |  | 1 by pole |  |
|  | • Overpressure valve |  |  | Specify |  |
|  | 10. Operating mechanism of the CB |  |  |  |  |
|  | • Type of operating mechanism |  |  | Specify |  |
|  | • Manufacturer reference |  |  |  |  |
|  | • Energy |  |  | Mechanical |  |
|  | • Auxiliary position contacts |  |  |  |  |
|  | - double opening type |  |  | Yes |  |
|  | - rated continuous current (class 1) |  | A | 10 |  |
|  | - rated capacity |  | A | 4A/220V |  |
|  | • Operations counter |  |  | Yes |  |
|  | • In/Out push button |  |  |  |  |
|  | - electrical |  |  | No |  |
|  | - mechanical |  |  | Yes |  |
|  | • Corrosion protection of the CB operating cabinet |  |  | Galvanised |  |
|  | • IP protection degree |  |  | ≥ IP55 |  |
|  | 11. Isolator characteristics |  |  |  |  |
|  | • Manufacturer |  |  | Specify |  |
|  | • Type |  |  | Specify |  |
|  | • Used material |  |  | Ceramic |  |
|  | • Insulated shed profile |  |  | Specify |  |
|  | • Between protective cover or lower terminal and earth |  |  |  |  |
|  | - Number of elements |  |  | 1 |  |
|  | - Total height |  | mm | Specify |  |
|  | - Minimum creeping distance |  | mm/kV | 31 |  |
|  | • Between entrance and exit |  |  |  |  |
|  | - number of elements |  |  | 1 |  |
|  | - total height |  | mm | Specify |  |
|  | - Minimum creeping distance |  | mm/kV | 31 |  |
|  | 12. Mechanical characteristics |  |  |  |  |
|  | • Weight of the CB |  | kg | Specify |  |
|  | • Weight of the CB operating cabinet |  | kg | Specify |  |
|  | • Weight of the CB central control cabinet |  | kg | Specify |  |
|  | • Minimum clearance between 2 different phases |  | mm | Specify |  |
|  | • HV connection terminals made of bored aluminium plates |  |  | Yes |  |
|  | 13. Paint and corrosion protection |  |  |  |  |
|  | • Oxydable metal parts |  |  | hot dip galvanizing |  |
|  | • Screws, nuts, bolts,…. |  |  |  |  |
|  | - for diameter ≤ M16 stainless steel |  |  | Yes |  |
|  | - for diameter > M16 hot dip galvanized steel and painted |  |  | Yes |  |
|  | • Frame of control panel galvanized |  |  | Yes |  |
|  | • Duplex principle (galvanized + paint) according GTS |  |  | Yes |  |
|  | • Final color paint |  |  |  |  |
|  | - pieces to earth |  |  | Specify |  |
|  | - live parts |  |  | Specify |  |
|  | - insulator's metal flanges |  |  | Specify |  |
|  | - grounded connections, metallic conductors,… free of paint |  |  |  |  |
|  |  |  |  |  |  |
|  | 14. Documents to be submitted |  |  |  |  |
|  | • Submital fase |  |  | 3 ex. |  |
|  | - General documentation |  |  |  |  |
|  | - List of references |  |  |  |  |
|  | - Type test reports |  |  |  |  |
|  | - datasheet completed |  |  |  |  |
|  | - dimensional drawing |  |  |  |  |
|  | • Ordering fase |  |  | 3 ex. |  |
|  | - operating instruction manual |  |  |  |  |
|  | - erection instruction manual |  |  |  |  |
|  | - maintenance instruction manual |  |  |  |  |
|  | - static and dynamic efforts |  |  |  |  |
|  | - drawings |  |  |  |  |
|  | - detailed dimensional drawing with an indication of weight and efforts |  |  |  |  |
|  | - drawing of the operating cubicle and central control cubicle |  |  |  |  |
|  | - drawing of the supporting structure (eventual) |  |  |  |  |
|  | - drawing of the rating plate |  |  |  |  |
|  | - LV diagrams |  |  |  |  |
|  | - drawing of electrical circuits |  |  |  |  |
|  | - principle diagram of the operating mechanism |  |  |  |  |
|  | • Completed Manufactuer final report including |  |  | 3 ex. |  |
|  | - operating instruction manual |  |  |  |  |
|  | - erection instruction manual |  |  |  |  |
|  | - maintenance instruction manual |  |  |  |  |
|  | - as built drawings and schematics |  |  |  |  |
|  | - factory test report |  |  |  |  |
|  | - report end assembly and testing on site |  |  |  |  |
|  | 15. Languages |  |  |  |  |
|  | • All documents establish in English |  |  | Yes |  |

| TECHNICAL SCHEDULE – Main Data Three phase Circuit Breaker – 220 kV – Three pole operated |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Description |  |  | Units | Imposed Values | Guaranteed Values* |
|  | 1. General characteristics |  |  |  |  |
|  | • Manufacturer |  |  | Specify |  |
|  | • Type |  |  | Specify |  |
|  | • Number of poles |  |  | 3 |  |
|  | • Indoor/Outdoor installation |  |  | Outdoor |  |
|  | • Quenching fluid |  |  | SF6 |  |
|  | • Network nominal voltage (Un) |  | kV | 220 |  |
|  | • Highest Operating Voltage (Um) |  | kV | 252 |  |
|  | • Rated frequency (fr) |  | Hz | 50 |  |
|  | • Number of breaking chamber per pole |  |  | 1 |  |
|  | • Action of CB operating mechanism |  |  | Three pole |  |
|  | • Insulator |  |  | Brown Porcelain |  |
|  | • Minimum phase creepage distance |  | mm/kV | 31 |  |
|  | 2. Circuit breaker class |  |  |  |  |
|  | • minimum number of operations |  |  | 10 000 |  |
|  | • minimum number of operations at rated current before first maintenance |  |  | 3000 |  |
|  | • minimum number of operations at rated short-circuit current for each phase before first maintenance |  |  | 12 |  |
|  | • Percent of yearly gas leakage |  | % | ≤ 0,3 |  |
|  | 3. Normal service conditions |  |  |  |  |
|  | • Ambient temperature range |  | °C | -35 to +50 |  |
|  | 4. Rated withstand currents |  |  |  |  |
|  | • Rated bus transfer current |  | A | 1600 |  |
|  | • Others bay |  | A | 1600 |  |
|  | • Rated buscoupler current |  | A | 3150 |  |
|  | • Rated short time withstand current |  | kA | 40 |  |
|  | • Rated peak withstand current |  | kA peak | 100 |  |
|  | • Rated duration of short circuit |  | s | 3 |  |
|  | 6. Rated voltage and rated insulation level |  |  |  |  |
|  | • Rated voltage for equipment (Ur) |  | kV | 245 |  |
|  | • Rated short duration power-frequency withstand voltage (AC) 1min-50Hz |  |  |  |  |
|  | - Between phases, phase to earth |  | kV | 460 |  |
|  | - Across open switching device |  | kV | 460 |  |
|  | • Rated lightning impulse withstand voltage (1,2/50µs) (Up) |  |  |  |  |
|  | - Between phases, phase to earth |  | kV peak | 1050 |  |
|  | - Across open switching device |  | kV peak | 1050 |  |
|  | 7. Tripping and closing characteristics |  |  |  |  |
|  | • Rated short circuit breaking current |  | kA | 40 |  |
|  | - time constant of the asymmetric component (dc) of the rated short circuit current |  | ms | 45 |  |
|  | • Fault at the HV terminals of the CB - rated transient recovery voltage with |  |  |  |  |
|  | - first-pole-to-clear-factor |  |  | 1,3 |  |
|  | 8. Operation durations |  |  |  |  |
|  | • Maximum closing time |  | ms | < 150 |  |
|  | • Maximum breaking time |  | ms | < 40 |  |
|  | • After a complete operating sequence O-0,3s-CO- 3min-CO, the operating mechanism should have enough energy left to proceed one more CO cycle within |  | s | Specify |  |
|  | 9. Technical characteristics of the auxiliary circuits |  |  |  |  |
|  | • Operating voltage of the closing circuits |  |  |  |  |
|  | - voltage |  | Vdc | 220 |  |
|  | - operating range |  | % | 85 to 110 |  |
|  | • Operating voltage of the tripping coils |  |  |  |  |
|  | - voltage |  | Vdc | 220 |  |
|  | - operating range |  | % | 70 to 110 |  |
|  | • Operating voltage of the motor |  |  |  |  |
|  | - voltage |  | Vdc | 220 |  |
|  | - operating range |  | % | 85 to 110 |  |
|  | • Voltage of the heating circuits |  | Vac | 230 |  |
|  | 11. Operating mechanism of the CB |  |  |  |  |
|  | • Manufacturer reference |  |  |  |  |
|  | -Three pole operated |  |  | Three pole |  |
|  | • Type (energy) |  |  | Spring |  |
|  | • Number of closing coils |  |  | 2 |  |
|  | • Number of trip coils |  |  | 2 |  |
|  | - number of free of potential open contacts (NO) |  |  | min. 5, specify |  |
|  | - number of free of potential close contacts (NC) |  |  | min. 5, specify |  |

| TECHNICAL SCHEDULE – Data for Information Three phase Circuit Breaker – 220 kV – Three pole operated |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Description |  |  | Units | Imposed Values | Guaranteed Values* |
|  | 1. General characteristics |  |  |  |  |
|  | • Place of manufacture |  |  | Specify |  |
|  | • Standards (latest edition) |  |  | IEC 62271-100 IEC 62271-1 |  |
|  | • First-pole-to-clear-factor |  |  | 1.3 |  |
|  | • Rated operating sequence O-0,3s-CO-3min-CO |  |  | Yes |  |
|  | • Number of grading capacitor per pole |  |  | N.A. |  |
|  | • Type of CB operating mechanism |  |  | Specify |  |
|  | 2. Circuit breaker class |  |  |  |  |
|  | • CB mechanicam life classidication |  |  | M1 |  |
|  | • CB electrical life classiffication |  |  | E1 |  |
|  | • CB restrike probability classification |  |  | C1 |  |
|  | 3. Normal service conditions(please refer to the site conditions of each substation) |  |  |  |  |
|  | • Ambient temperature range |  | °C |  |  |
|  | • Relative humidity |  | % |  |  |
|  | • Maximum altitude |  | m |  |  |
|  | • Maximum ice coating |  | mm |  |  |
|  | • Maximum pressure of the wind speed |  | Pa |  |  |
|  | • Solar radiation |  | W/m² |  |  |
|  | 4. Overload capabilities |  |  |  |  |
|  | • Permissible overload currents in accordance with the standard IEC 62271-1 |  |  | Yes |  |
|  | 5. Rated voltage and rated insulation level |  |  |  |  |
|  | • Radio disturbance voltage at 1.1 U / -1MHz |  | μV | ≤ 2500 max. |  |
|  | 6. Tripping and closing characteristics |  |  |  |  |
|  | • Rated short circuit breaking current |  |  |  |  |
|  | - minimum opening time (m.o.t) |  | ms | Specify |  |
|  | - percentage of the asymmetric component ( at 10 ms + m.o.t) |  | % | Specify |  |
|  | - total I |  | kA | Specify |  |
|  | • Fault at the HV terminals of the CB - rated transient recovery voltage with |  |  |  |  |
|  | - rate of rise of recovery voltage (RRRV) |  | kV/µs | 2 |  |
|  | - transient recovery voltage peak value |  | kV | 364 |  |
|  | • Rated peak short circuit making current |  | kA peak | 80 |  |
|  | • On HV line, close fault occuring - rated transient recovery voltage |  |  |  |  |
|  | - fault on line side |  |  |  |  |
|  | . full wave impedance |  | Ω | 450 |  |
|  | . rate of rise factor of the recovery voltage |  | kV/μs.kA | 0,2 |  |
|  | . rated peak factor |  |  | 1,6 |  |
|  | - fault at source side (according IEC 56, table IV) |  |  |  |  |
|  | . rate of rise of recovery voltage |  | kV/µs | 2 |  |
|  | . peak value of the transient recovery voltage |  | kV | 280 |  |
|  | • Rated out-of-phase breaking current in discripency with a rated recovery voltage 2 x U /. |  | kA | 7.875 |  |
|  | • Rated line-charging breaking current (no load) |  |  |  |  |
|  | - rated short-circuit breaking current |  | A | 125. |  |
|  | - maximum overvoltage guarented without arcing |  | kV peak | < 2.5 x 245 |  |
|  | • Rated cable-charging breaking current no load) |  |  |  |  |
|  | - rated short-circuit breaking current |  | A | 250. |  |
|  | - maximum overvoltage guarented without arcing |  | kV peak | < 2.5 x 245 |  |
|  | • Rated maximum capacitive breaking current |  |  |  |  |
|  | - rated short-circuit breaking current |  | A | 400. |  |
|  | - maximum overvoltage guarented without arcing |  | kV peak | < 2.5 x 245 |  |
|  | • Rated small inductive breaking current |  |  |  |  |
|  | - rated short-circuit breaking current |  | A | Specify. |  |
|  | - maximum overvoltage guarented without arcing |  | kV peak | < 2.5 x 245 |  |
|  | • Number of operations taking into account the maintenance program specified by the manufacturer |  |  | min.2000 (class M1) |  |
|  | 7. Operation durations |  |  |  |  |
|  | • Maximum opening time |  | ms | Specify |  |
|  | • Maximum dead time (between break and restore) |  | ms | Specify |  |
|  | • Maximum discrepancy between |  |  |  |  |
|  | - the breaking chamber of a same pole |  |  |  |  |
|  | . during closing operation |  | ms | N.A. |  |
|  | . during opening operation |  | ms | N.A. |  |
|  | - the poles of different phases |  |  |  |  |
|  | . during closing operation |  | ms | 5 |  |
|  | . during opening operation |  | ms | 3.33 |  |
|  | • Minimal duration of the switching impuls for |  |  |  |  |
|  | - closing coil |  | ms | Specify |  |
|  | - trip coil |  | ms | Specify |  |
|  | 8. Technical characteristics of the auxiliary circuits |  |  |  |  |
|  | • Power consumption |  |  |  |  |
|  | - closing coil |  | W | Specify |  |
|  | - tripping coil |  | W | Specify |  |
|  | - motor of the operating mechanism |  | W | Specify |  |
|  | - continuous heating |  | W | Specify |  |
|  | - heating with thermostat |  | W | Specify |  |
|  | 9. Breaking chamber |  |  |  |  |
|  | • Quenching fluid |  |  | SF6 |  |
|  | - Filling in pressure |  | MPa (abs) | Specify |  |
|  | - first alarm pressure |  | MPa (abs) | Specify |  |
|  | - second alarm pressur (lockout or trip) |  | MPa (abs) | Specify |  |
|  | • Number of breaking chamber per poles of the CB |  |  | 1 |  |
|  | • Rated value of the grading capacitor |  | pF | N.A. |  |
|  | • Gas quantity per pole of the CB |  | kg | Specify |  |
|  | • Total course of the moving contact in one breaking chamber |  | mm | Specify |  |
|  | • Distance between the mains contact in one breaking chamber |  | mm | Specify |  |
|  | • Operating speed of the moving contact |  |  |  |  |
|  | - closing time |  | m/s | Specify |  |
|  | - breaking time |  | m/s | Specify |  |
|  | • Densimeter of temperature compensated manometer (SF6 monitoring) |  |  | 1 by pole |  |
|  | • Overpressure valve |  |  | Specify |  |
|  | 10. Operating mechanism of the CB |  |  |  |  |
|  | • Type of operating mechanism |  |  | Specify |  |
|  | • Energy |  |  | Mechanical |  |
|  | • Auxiliary position contacts |  |  |  |  |
|  | - double opening type |  |  | Yes |  |
|  | - rated continuous current (class 1) |  | A | 10 |  |
|  | - rated capacity |  | A | 4A/220V |  |
|  | • Operations counter |  |  | Yes |  |
|  | • In/Out push button |  |  |  |  |
|  | - electrical |  |  | No |  |
|  | - mechanical |  |  | Yes |  |
|  | • Corrosion protection of the CB local cabinet |  |  | Galvanised |  |
|  | • IP protection degree |  |  | ≥ IP55 |  |
|  | 11. Isolator characteristics |  |  |  |  |
|  | • Manufacturer |  |  | Specify |  |
|  | • Type |  |  | Specify |  |
|  | • Used material |  |  | Ceramic |  |
|  | • Insulated shed profile |  |  | Specify |  |
|  | • Between protective cover or lower terminal and earth |  |  |  |  |
|  | - Number of elements |  |  | 1 |  |
|  | - Total height |  | mm | Specify |  |
|  | - Minimum creeping distance |  | mm/kV | 31 |  |
|  | • Between entrance and exit |  |  |  |  |
|  | - number of elements |  |  | 1 |  |
|  | - total height |  | mm | Specify |  |
|  | - Minimum creeping distance |  | mm/kV | 31 |  |
|  | 12. Mechanical characteristics |  |  |  |  |
|  | • Weight of the CB |  | kg | Specify |  |
|  | • Weight of the CB operating cabinet |  | kg | Specify |  |
|  | • Minimum clearance between 2 different phases |  | mm | Specify |  |
|  | • HV connection terminals made of bored aluminium plates |  |  | Yes |  |
|  | 13. Paint and corrosion protection |  |  |  |  |
|  | • Oxydable metal parts |  |  | hot dip galvanizing |  |
|  | • Screws, nuts, bolts,…. |  |  |  |  |
|  | - for diameter ≤ M16 stainless steel |  |  | Yes |  |
|  | - for diameter > M16 hot dip galvanized steel and painted |  |  | Yes |  |
|  | • Frame of control panel galvanized |  |  | Yes |  |
|  | • Duplex principle (galvanized + paint) according GTS |  |  | Yes |  |
|  | • Final color paint |  |  |  |  |
|  | - pieces to earth |  |  | Specify |  |
|  | - live parts |  |  | Specify |  |
|  | - insulator's metal flanges |  |  | Specify |  |
|  | - grounded connections, metallic conductors,… free of paint |  |  |  |  |
|  | 14. Documents to be submitted |  |  |  |  |
|  | • Submital fase |  |  | 3 ex. |  |
|  | - General documentation |  |  |  |  |
|  | - List of references |  |  |  |  |
|  | - Type test reports |  |  |  |  |
|  | - datasheet completed |  |  |  |  |
|  | - dimensional drawing |  |  |  |  |
|  | • Ordering fase |  |  | 3 ex. |  |
|  | - operating instruction manual |  |  |  |  |
|  | - erection instruction manual |  |  |  |  |
|  | - maintenance instruction manual |  |  |  |  |
|  | - static and dynamic efforts |  |  |  |  |
|  | - drawings |  |  |  |  |
|  | - detailed dimensional drawing with an indication of weight and efforts |  |  |  |  |
|  | - drawing of the operating cabinet |  |  |  |  |
|  | - drawing of the supporting structure (eventual) |  |  |  |  |
|  | - drawing of the rating plate |  |  |  |  |
|  | - LV diagrams |  |  |  |  |
|  | - drawing of electrical circuits |  |  |  |  |
|  | - principle diagram of the operating mechanism |  |  |  |  |
|  | • Completed Manufactuer final report including |  |  | 3 ex. |  |
|  | - operating instruction manual |  |  |  |  |
|  | - erection instruction manual |  |  |  |  |
|  | - maintenance instruction manual |  |  |  |  |
|  | - as built drawings and schematics |  |  |  |  |
|  | - factory test report |  |  |  |  |
|  | - report end assembly and testing on site |  |  |  |  |
|  | 15. Languages |  |  |  |  |
|  | • All documents establish in English |  |  | Yes |  |

| TECHNICAL SCHEDULE – Main Data Inductive Current Transformer 220kV |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Description |  |  | Units | Imposed Values | Guaranteed Values |
|  | 1. General characteristics |  |  |  |  |
|  | • Manufacturer |  |  | Specify |  |
|  | • Type |  |  | Single Phase,Oil Immersed, Inductive |  |
|  | • Indoor/Outdoor installation |  |  | Outdoor |  |
|  | 2. Normal service conditions |  |  |  |  |
|  | • Ambient temperature range |  | °C | -35 to +50 |  |
|  | 3. Electrical characteristics |  |  |  |  |
|  | • Rated Frequency |  | Hz | 50 |  |
|  | • Service voltage |  | kV | 220 |  |
|  | • Rated voltage (Ur) |  | kV | 252 |  |
|  | • Rated short duration power-frequency withstand voltage (AC) 1min-50Hz (Ud) |  | kV | 460 |  |
|  | • Rated lightning impulse withstand voltage (Up) |  | kV peak | 1050 |  |
|  | • Rated short time withstand current (3s) |  | kA | 40 |  |
|  | • Rated peak withstand current |  | kA | 100 |  |
|  | • Permanently permissible primary overcurrent |  |  | 1.2 In |  |
|  | • Secondary windings |  |  |  |  |
|  | - Secondary nominal current |  | A | 5 |  |
|  | - Rated insulation voltage |  | kV | 0.72 |  |
|  | - Short duration power-frequency withstand voltage (AC) 1min-50Hz |  | kV | 3 |  |
|  | 4. Windings characteristics |  |  |  |  |
|  | • Turn ratio |  |  |  |  |
|  | - Core nr.1 (meetering) |  | A | 600-800-1000-1200 |  |
|  | - Core nr.2 (measure) |  | A | 600-800-1000-1200 |  |
|  | - Core nr.3 (protection) |  | A | 600-800-1000-1200 |  |
|  | - Core nr.4 (protection) |  | A | 600-800-1000-1200 |  |
|  | - Core nr.5 (protection) |  | A | 600-800-1000-1200 |  |
|  | • Accuracy burden |  |  |  |  |
|  | - Core nr.1 (metering) |  | VA | 50 |  |
|  | - Core nr.2 (measure) |  | VA | 50 |  |
|  | - Core nr.3 (protection) |  | VA | 50 |  |
|  | - Core nr.4 (protection) |  | VA | 50 |  |
|  | - Core nr.5 (protection) |  | VA | 50 |  |
|  | • Accuracy class |  |  |  |  |
|  | - Core nr.1 (metering) |  |  | 0.2 |  |
|  | - Core nr.2 (measure) |  |  | 0.5 |  |
|  | - Core nr.3 (protection - 5P) |  |  | 5P30 |  |
|  | - Core nr.4 (protection - 5P) |  |  | 5P30 |  |
|  | - Core nr.5 (protection - 5P) |  |  | 5P30 |  |
|  | 5. Insulators characteritics |  |  |  |  |
|  | • Used material |  |  | Porcelain – Brown |  |
|  | • Minimum nominal creeping distance |  | mm | 7812 |  |
|  | • Minimum Spark Gap |  | mm | 2200 |  |

| TECHNICAL SCHEDULE – Data for Information Inductive Current Transformer 220kV |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Description |  |  | Units | Imposed Values | Guaranteed Values |
|  | 1. General characteristics |  |  |  |  |
|  | • Place of manufacture |  |  | Specify |  |
|  | • Type |  |  | Specify |  |
|  | • Standards (latest edition) |  |  | IEC 61869-1 and 2 |  |
|  | 2. Normal service conditions(please refer to the site conditions of each substation) |  |  |  |  |
|  | • Ambient temperature range |  | °C |  |  |
|  | • Relative humidity |  | % |  |  |
|  | • Maximum altitude |  | m |  |  |
|  | • Maximum ice coating |  | mm |  |  |
|  | • Maximum pressure of the wind speed |  | Pa |  |  |
|  | • Solar radiation |  | W/m² |  |  |
|  | 3. Overload conditions |  |  |  |  |
|  | • Permissible overload currents in accordance with the standard IEC 62271-1 |  |  | Yes |  |
|  | 4. Electromagnetic Unit |  |  |  |  |
|  | • Internal insulation |  |  | Specify |  |
|  | • Oil |  |  |  |  |
|  | - type |  |  | Specify |  |
|  | - supplier and oil reference |  |  | Specify |  |
|  | • Hermeticity type system |  |  | Specify |  |
|  | 5. Insulators characteritics |  |  |  |  |
|  | • Manufacturer |  |  | Specify |  |
|  | • Number of elements |  |  | 1 |  |
|  | 6. Mechanical characteristics |  |  |  |  |
|  | • Total height |  | mm | Specify |  |
|  | • Total weight |  | kg | Specify |  |
|  | • Oil weight |  | kg | Specify |  |
|  | • Primary terminals |  |  |  |  |
|  | - alloy |  |  | Tinned copper |  |
|  | - diameter |  | mm | Specify |  |
|  | - Contact length |  | mm | Specify |  |
|  | - Height (axis ground surface - primary terminal) |  | mm | Specify |  |
|  | • Secondary terminals |  |  |  |  |
|  | - Earthing bar and removable bridges |  |  | Yes |  |
|  | 7. Paint and corrosion protection |  |  |  |  |
|  | • Oxydable metal parts |  |  | hot dip galvanizing |  |
|  | • Screws, nuts, bolts,…. |  |  |  |  |
|  | - for diameter ≤ M16 stainless steel |  |  | Yes |  |
|  | - for diameter > M16 hot dip galvanized steel and painted |  |  | Yes |  |
|  | • Frame of control panel galvanized |  |  | Yes |  |
|  | • Duplex principle (galvanized + paint) according GTS |  |  | Yes |  |
|  | • Final color paint |  |  |  |  |
|  | - pieces to earth |  |  | Specify |  |
|  | - live parts |  |  | Specify |  |
|  | - insulator's metal flanges |  |  | Specify |  |
|  | - grounded connections, metallic conductors,… free of paint |  |  |  |  |
|  | 8. Documents to be submitted |  |  |  |  |
|  | • Submital fase |  |  | 3 ex. |  |
|  | - General documentation |  |  |  |  |
|  | - List of references |  |  |  |  |
|  | - Type test reports |  |  |  |  |
|  | - datasheet completed |  |  |  |  |
|  | - dimensional drawing |  |  |  |  |
|  | • Ordering fase |  |  | 3 ex. |  |
|  | - erection instruction manual |  |  |  |  |
|  | - maintenance instruction manual |  |  |  |  |
|  | - static and dynamic efforts |  |  |  |  |
|  | - drawings |  |  |  |  |
|  | - detailed dimensional drawing with an indication of weight and efforts |  |  |  |  |
|  | - drawing of the LV terminals cabinet |  |  |  |  |
|  | - drawing of the rating plate |  |  |  |  |
|  | • Completed Manufactuer final report including |  |  | 3 ex. |  |
|  | - erection instruction manual |  |  |  |  |
|  | - maintenance instruction manual |  |  |  |  |
|  | - as built drawings and schematics |  |  |  |  |
|  | - factory test report |  |  |  |  |
|  | 9. Languages |  |  |  |  |
|  | • All documents establish in English |  |  | Yes |  |

| TECHNICAL SCHEDULE – Main Data |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Combinated Disconnector and Earthing - 220kV |  |  |  |  |  |
| Description |  |  | Units | Imposed Values | Guaranteed Values* |
|  | 1. General characteristics |  |  |  |  |
|  | • Manufacturer |  |  | Specify |  |
|  | • Type |  |  | Specify |  |
|  | • Number of poles |  |  | 3 |  |
|  | • Indoor/Outdoor installation |  |  | Outdoor |  |
|  | • Maximum opening time |  | s | 10 |  |
|  | • Maximum closing time |  | s | 10 |  |
|  | • Number of switching events until the first maintenance |  |  | 1000 |  |
|  | • Insulator type |  |  | Brown Porcelain |  |
|  | • Minimum nominal creeping distance |  | mm / kV | 31 |  |
|  | 2. Normal service conditions |  |  |  |  |
|  | • Ambient temperature range |  | °C | -35 to +50 |  |
|  | 3. Currents Characteristics |  |  |  |  |
|  | • Rated current (In) |  | A | 1600 |  |
|  | • Rated buscoupler current |  | A | 3150 |  |
|  | • Rated short time withstand current |  | kA | 40 |  |
|  | • Rated peak withstand current |  | kA peak | 100 |  |
|  | • Rated duration of short circuit |  | s | 3 |  |
|  | 4. Rated voltage and rated insulation level |  |  |  |  |
|  | • Service voltage |  | kV | 220 |  |
|  | • Rated voltage (Ur) |  | kV | 252 |  |
|  | • Rated frequency |  | Hz | 50 |  |
|  | • Rated duration short-duration power-frequency withstand voltage (Ud) |  |  |  |  |
|  | - Phase to earth |  | kV | 460 |  |
|  | - Across open switching device |  | kV | 530 |  |
|  | • Rated lightning impulse withstand voltage (1,2/50µs) (Up) |  |  |  |  |
|  | - Phase to earth |  | kV peak | 1050 |  |
|  | - Across open switching device |  | kV peak | 1200 |  |
|  | 5. Disconnector operating device |  |  |  |  |
|  | Main blades |  |  |  |  |
|  | • Type of operating device |  |  |  |  |
|  | • Three or single pole operated |  |  | three pole |  |
|  | • Motorized or manual operated |  |  | motorized |  |
|  | • Motorization |  |  |  |  |
|  | - Rated voltage of the motor |  | Vdc | 220 |  |
|  | • Number of potential free auxiliary contacts |  |  |  |  |
|  | - Closed – Open - Open: COO |  |  | 4 |  |
|  | - Open – Open - Closed: OOC |  |  | 4 |  |
|  | - Open – Closed - Closed: OCC |  |  | 2 |  |
|  | - Open – Closed - Open: OCO |  |  | 2 |  |
|  | • Heating |  |  |  |  |
|  | - Rated voltage |  | Vca | 230 |  |
|  | Earth blades for lines |  |  |  |  |
|  | • Type of operating device |  |  |  |  |
|  | • Three or single pole operated |  |  | three pole |  |
|  | • Motorized or manual operated |  |  | motorized |  |
|  | • Motorization |  |  |  |  |
|  | - Rated voltage of the motor |  | Vdc | 220 |  |
|  | • Number of potential free auxiliary contacts |  |  |  |  |
|  | - Closed – Open - Open: COO |  |  | 4 |  |
|  | - Open – Open - Closed: OOC |  |  | 4 |  |
|  | - Open – Closed - Closed: OCC |  |  | 2 |  |
|  | - Open – Closed - Open: OCO |  |  | 2 |  |
|  | • Heating |  |  |  |  |
|  | - Rated voltage |  | Vca | 230 |  |

| TECHNICAL SCHEDULE – Data for Information |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Combinated Disconnector and Earthing - 220kV |  |  |  |  |  |
| Description |  |  | Units | Imposed Values | Guaranteed Values* |
|  | 1. General characteristics |  |  |  |  |
|  | • Place of manufacture |  |  | Specify |  |
|  | • Standards (latest edition) |  |  | IEC 62271-102 |  |
|  | • Single break disconnector |  |  | Yes |  |
|  | • Earthing switch on line side |  |  | Yes |  |
|  | • Earthing switch on CB side |  |  | Yes |  |
|  | • Class |  |  |  |  |
|  | - Main blades |  |  | M1 |  |
|  | - Earth blades |  |  | E1 |  |
|  | 2. Normal service conditions(please refer to the site conditions of each substation) |  |  |  |  |
|  | • Ambient temperature range |  | °C |  |  |
|  | • Relative humidity |  | % |  |  |
|  | • Maximum altitude |  | m |  |  |
|  | • Maximum ice coating |  | mm |  |  |
|  | • Maximum pressure of the wind speed |  | Pa |  |  |
|  | • Solar radiation |  | W/m² |  |  |
|  | 3. Currents Characteristics |  |  |  |  |
|  | • Maximum temperature rise at In (t° ambient: 45°C) |  |  | Specify |  |
|  | 4. Rated voltage and rated insulation level |  |  |  |  |
|  | • Contact resistance |  |  |  |  |
|  | - Main blades |  | μΩ | Specify |  |
|  | - Earth blades |  | μΩ | Specify |  |
|  | 5. Overload conditions |  |  |  |  |
|  | • Permissible overload currents in accordance with the standard IEC 62271-1 |  |  | Yes |  |
|  | 6. Insulators characteritics |  |  |  |  |
|  | • Manufacturer |  |  | Specify |  |
|  | • Type (based IEC) |  |  | Specify |  |
|  | • Used material |  |  | Ceramic |  |
|  | • Profile |  |  | Specify |  |
|  | • Number of elements |  |  | 1 |  |
|  | • Height |  | mm | Specify |  |
|  | • Weight |  | kg | Specify |  |
|  | 7. Disconnector operating device |  |  |  |  |
|  | Main blades |  |  |  |  |
|  | • Type (manufacturer reference) |  |  | Specify |  |
|  | • Motorization |  |  |  |  |
|  | - Rated voltage of the motor |  | Vdc | 220 |  |
|  | - Tolerance |  | % | 85 - 110 |  |
|  | - Capacity |  | W | Specify |  |
|  | - Motor current |  | A | Specify |  |
|  | - Maximum motor current |  | A | Specify |  |
|  | - Rated current for operation at maximum torque |  | A | Specify |  |
|  | - Switching time: |  |  |  |  |
|  | - Closing time of the disconnector |  | s | Specify |  |
|  | - Opening time of the disconnector |  | s | Specify |  |
|  | • Emergency manual operating device available |  |  | Yes |  |
|  | - Type of operating device (crank,….) |  |  | Specify |  |
|  | - Maximal torque needed for manual opening |  | Nm | Specify |  |
|  | - Maximal torque needed for manual closing |  | Nm | Specify |  |
|  | - Maximal operation height above ground level |  | mm | 1500 |  |
|  | • Number of potential free auxiliary contacts |  |  |  |  |
|  | - Closed – Open - Open: COO |  |  | 4 |  |
|  | - Open – Open - Closed: OOC |  |  | 4 |  |
|  | - Open – Closed - Closed: OCC |  |  | 2 |  |
|  | - Open – Closed - Open: OCO |  |  | 2 |  |
|  | - Breaking capacity |  |  | 4 A at 220 V |  |
|  | - Minimum rated current |  |  | 10 A (class 1) |  |
|  | • Heating |  |  |  |  |
|  | - Rated voltage |  | Vca | 230 |  |
|  | - Tolerance |  | % | 85 - 110 |  |
|  | - Power |  | W | Specify |  |
|  | • Protection level |  |  | ≥IP 55 |  |
|  | Earth blades for lines |  |  |  |  |
|  | • Type (manufacturer reference) |  |  | Specify |  |
|  | • Motorization |  |  |  |  |
|  | - Rated voltage of the motor |  | Vdc | 220 |  |
|  | - Tolerance |  | % | 85 - 110 |  |
|  | - Capacity |  | W | Specify |  |
|  | - Motor current |  | A | Specify |  |
|  | - Maximum motor current |  | A | Specify |  |
|  | - Rated current for operation at maximum torque |  | A | Specify |  |
|  | - Switching time: |  |  |  |  |
|  | - Closing time of the earth switch |  | s | Specify |  |
|  | - Opening time of the earth switch |  | s | Specify |  |
|  | • Emergency manual operating device available |  |  | Yes |  |
|  | - Type of operating device (crank,….) |  |  | Specify |  |
|  | - Maximal torque needed for manual opening |  | Nm | Specify |  |
|  | - Maximal torque needed for manual closing |  | Nm | Specify |  |
|  | - Maximal operation height above ground level |  | mm | 1500 |  |
|  | • Number of potential free auxiliary contacts |  |  |  |  |
|  | - Closed – Open - Open: COO |  |  | 4 |  |
|  | - Open – Open - Closed: OOC |  |  | 4 |  |
|  | - Open – Closed - Closed: OCC |  |  | 2 |  |
|  | - Open – Closed - Open: OCO |  |  | 2 |  |
|  | - Breaking capacity |  |  | 4 A at 220 V |  |
|  | - Minimum rated current |  |  | 10 A (class 1) |  |
|  | • Heating |  |  |  |  |
|  | - Rated voltage |  | Vca | 230 |  |
|  | - Tolerance |  | % | 85 - 110 |  |
|  | - Power |  | W | Specify |  |
|  | • Protection level |  |  | ≥IP 55 |  |
|  | Earth blades for Breaker Maintenance and Busbar |  |  |  |  |
|  | • Type of operating device |  |  |  |  |
|  | • Three or single pole operated |  |  | three pole |  |
|  | • Motorized or manual operated |  |  | manual |  |
|  | • Type (manufacturer reference) |  |  | Specify |  |
|  | - Maximal torque needed for manual opening |  | Nm | Specify |  |
|  | - Maximal torque needed for manual closing |  | Nm | Specify |  |
|  | - Maximal operation height above ground level |  | mm | 1500 |  |
|  | • Number of potential free auxiliary contacts |  |  |  |  |
|  | - Closed – Open - Open: COO |  |  | 4 |  |
|  | - Open – Open - Closed: OOC |  |  | 4 |  |
|  | - Breaking capacity |  |  | 4 A at 220 V |  |
|  | - Minimum rated current |  |  | 10 A (class 1) |  |
|  | • Heating |  |  |  |  |
|  | - Rated voltage |  | Vca | 230 |  |
|  | - Tolerance |  | % | 85 - 110 |  |
|  | - Power |  | W | Specify |  |
|  | • Protection level |  |  | ≥IP 55 |  |
|  | 8. Safety and locking |  |  |  |  |
|  | Main blades |  |  |  |  |
|  | • Normal electrical operated mechanism |  |  |  |  |
|  | - Mechanical locking device placed on motor drive |  |  | Yes |  |
|  | - Motor circuit interrupted by the locking device |  |  | Yes |  |
|  | - Padlockable mechanical locking device in open and closed position (padlocking Ø8mm possible) |  |  | Yes |  |
|  | • Manual drive (if applicable) |  |  | N.A. |  |
|  | - Locking coil in combination with push button |  |  | N.A. |  |
|  | - Supply voltage |  | Vdc | N.A. |  |
|  | - Padlockable mechanical locking device in open and closed position (padlocking Ø8mm possible) |  |  | N.A. |  |
|  | Earth blades for lines |  |  |  |  |
|  | • Normal electrical operated mechanism |  |  |  |  |
|  | - Mechanical locking device placed on motor drive |  |  | Yes |  |
|  | - Motor circuit interrupted by the locking device |  |  | Yes |  |
|  | - Padlockable mechanical locking device in open and closed position (padlocking Ø8mm possible) |  |  | Yes |  |
|  | • Manual drive (if applicable) |  |  | N.A. |  |
|  | - Locking coil in combination with push button |  |  | N.A. |  |
|  | - Supply voltage |  | Vdc | N.A. |  |
|  | - Padlockable mechanical locking device in open and closed position (padlocking Ø8mm possible) |  |  | N.A. |  |
|  | Earth blades for Breaker maintenance and Busbar |  |  |  |  |
|  | - Locking coil in combination with push button |  |  | Yes |  |
|  | - Supply voltage |  | Vdc | 220 |  |
|  | - Padlockable mechanical locking device in open and closed position (padlocking Ø8mm possible) |  |  | Yes |  |
|  | Main blades and Earth blades |  |  |  |  |
|  | - Mechanical interlock between main and earth blades |  |  |  |  |
|  | 9. Ergonomics |  |  |  |  |
|  | • Minimum height from ground or circulation level |  |  |  |  |
|  | - bottom skirt of the isolator |  | mm | 2500 |  |
|  | - vertical distance of life part |  | mm | 4500 |  |
|  | • Preferential height from ground or circulation level |  |  |  |  |
|  | - bottom side of the drives |  | mm | 1000 < H < 1600 |  |
|  | - top side of the drives |  | mm | Maximum 2500 |  |
|  | - door handles |  | mm | Maximum 1800 |  |
|  | 10. Mechanical characteristics |  |  |  |  |
|  | • Weight of the complete disconnector |  | kg | Specify |  |
|  | • Weight of the operating mechanisms |  |  |  |  |
|  | - Weight of the main blades operating mechanism |  | kg | Specify |  |
|  | - Weight of the earth blades operating mechanism |  | kg | Specify |  |
|  | 11. Construction details |  |  |  |  |
|  | Main blades |  |  |  |  |
|  | - Used material for contact (Al, electroplated silver or tinned copper) |  |  | Specify |  |
|  | - Contact type |  |  | Specify |  |
|  | - Maximum temperature rise at In (t° ambient: 45°C) |  |  | Specify |  |
|  | - Number of contact fingers |  |  | Specify |  |
|  | - Contact pressure by finger |  | daN | Specify |  |
|  | - Type of electrical connection between elements |  |  | Specify |  |
|  | • HV Terminals |  |  |  |  |
|  | - Diameter (according Inom) |  |  | Specify |  |
|  | - Used material for contact (Al, electroplated silver or tinned copper) |  |  | Specify |  |
|  | - Length |  |  | Specify |  |
|  | - Supply all the parts needed for connecting connection |  |  | Yes |  |
|  | Earth blades |  |  |  |  |
|  | - Used material for contact (Al, electroplated silver or tinned copper) |  |  | Specify |  |
|  | - Contact type |  |  | Specify |  |
|  | - Number of contact fingers |  |  | Specify |  |
|  | - Contact pressure by finger |  | daN | Specify |  |
|  | 12. Paint and corrosion protection |  |  |  |  |
|  | • Oxydable metal parts |  |  | hot dip galvanizing |  |
|  | • Screws, nuts, bolts,…. |  |  |  |  |
|  | - for diameter ≤ M16 stainless steel |  |  | Yes |  |
|  | - for diameter > M16 hot dip galvanized steel and painted |  |  | Yes |  |
|  | • Frame of control panel galvanized |  |  | Yes |  |
|  | • Duplex principle (galvanized + paint) according GTS |  |  | Yes |  |
|  | • Final color paint |  |  |  |  |
|  | - pieces to earth |  |  | Specify |  |
|  | - live parts |  |  | Specify |  |
|  | - insulator's metal flanges |  |  | Specify |  |
|  | - grounded connections, metallic conductors,… free of paint |  |  |  |  |
|  |  |  |  |  |  |
|  | 13. Documents to be submitted |  |  |  |  |
|  | • Submital fase |  |  | 3 ex. |  |
|  | - General documentation |  |  |  |  |
|  | - List of references |  |  |  |  |
|  | - Type test reports |  |  |  |  |
|  | - datasheet completed |  |  |  |  |
|  | - dimensional drawing |  |  |  |  |
|  | • Ordering fase |  |  | 3 ex. |  |
|  | - operating instruction manual |  |  |  |  |
|  | - erection instruction manual |  |  |  |  |
|  | - maintenance instruction manual |  |  |  |  |
|  | - static and dynamic efforts |  |  |  |  |
|  | - drawings |  |  |  |  |
|  | - detailed dimensional drawing with an indication of weight and efforts |  |  |  |  |
|  | - drawing of the operating cubicles |  |  |  |  |
|  | - drawing of the rating plate |  |  |  |  |
|  | - LV diagrams |  |  |  |  |
|  | - drawing of electrical circuits |  |  |  |  |
|  | - principle diagram of the operating mechanism for main blades |  |  |  |  |
|  | - principle diagram of the operating mechanism for earth blades |  |  |  |  |
|  | • Completed Manufactuer final report including |  |  | 3 ex. |  |
|  | - operating instruction manual |  |  |  |  |
|  | - erection instruction manual |  |  |  |  |
|  | - maintenance instruction manual |  |  |  |  |
|  | - as built drawings and schematics |  |  |  |  |
|  | - factory test report |  |  |  |  |
|  | 14. Languages |  |  |  |  |
|  | • All documents establish in English |  |  | Yes |  |

| TECHNICAL SCHEDULE – Main Data |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Disconnector – 1 Pole - 220kV |  |  |  |  |  |
| Description |  |  | Units | Imposed Values | Guaranteed Values* |
|  | 1. General characteristics |  |  |  |  |
|  | • Manufacturer |  |  | Specify |  |
|  | • Type |  |  | Specify |  |
|  | • Number of poles |  |  | 1 |  |
|  | • Indoor/Outdoor installation |  |  | Outdoor |  |
|  | • Maximum opening time |  | s | 10 |  |
|  | • Maximum closing time |  | s | 10 |  |
|  | • Number of switching events until the first maintenance |  |  | 1000 |  |
|  | • Insulator type |  |  | Brown Porcelain |  |
|  | • Minimum nominal creeping distance |  | mm / kV | 31 |  |
|  | 2. Normal service conditions |  |  |  |  |
|  | • Ambient temperature range |  | °C | -35 to +50 |  |
|  | 3. Currents characteristics |  |  |  |  |
|  | • Rated bay current |  | A | 1600 |  |
|  | • Rated buscoupler current |  | A | 3150 |  |
|  | • Rated short time withstand current |  | kA | 40 |  |
|  | • Rated peak withstand current |  | kA peak | 100 |  |
|  | • Rated duration of short circuit |  | s | 3 |  |
|  | 4. Rated voltage and rated insulation level |  |  |  |  |
|  | • Network nominal voltage |  | kV | 220 |  |
|  | • Rated voltage (Ur) |  | kV | 252 |  |
|  | • Rated frequency |  | Hz | 50 |  |
|  | • Rated duration short-duration power-frequency withstand voltage (Ud) |  |  |  |  |
|  | - Phase to earth |  | kV | 460 |  |
|  | - Across open switching device |  | kV | 530 |  |
|  | • Rated lightning impulse withstand voltage (1,2/50µs) (Up) |  |  |  |  |
|  | - Phase to earth |  | kV peak | 1050 |  |
|  | - Across open switching device |  | kV peak | 1200 |  |
|  | 5. Operating device |  |  |  |  |
|  | • Type of operating device |  |  |  |  |
|  | - Single pole operated |  |  | YES |  |
|  | - Motorized or manual operated |  |  | motorized |  |
|  | • Motorization |  |  |  |  |
|  | - Rated voltage of the motor |  | Vdc | 220 |  |
|  | • Number of potential free auxiliary contacts |  |  |  |  |
|  | - Closed – Open - Open: COO |  |  | 4 |  |
|  | - Open – Open - Closed: OOC |  |  | 4 |  |
|  | - Open – Closed - Closed: OCC |  |  | 2 |  |
|  | - Open – Closed - Open: OCO |  |  | 2 |  |
|  | - Breaking capacity |  |  | 4 A at 220 V |  |
|  | - Minimum rated current |  |  | 10 A (class 1) |  |
|  | • Heating |  |  |  |  |
|  | - Rated voltage |  | Vca | 230 |  |

| TECHNICAL SCHEDULE – Data for Information |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Disconnector – 1 Pole - 220kV |  |  |  |  |  |
| Description |  |  | Units | Imposed Values | Guaranteed Values* |
|  | 1. General characteristics |  |  |  |  |
|  | • Place of manufacture |  |  | Specify |  |
|  | • Standards (latest edition) |  |  | IEC 62271-102 |  |
|  | • Class |  |  |  |  |
|  | - Main blades |  |  | M1 |  |
|  | 2. Normal service conditions(please refer to the site conditions of each substation) |  |  |  |  |
|  | • Ambient temperature range |  | °C | -35 to +50 |  |
|  | • Relative humidity |  | % | 50 |  |
|  | • Maximum altitude |  | m | < 1000 |  |
|  | • Maximum ice coating |  | mm | 8 |  |
|  | • Maximum pressure of the wind speed |  | Pa | ≤1030 (44,4m/s) |  |
|  | • Solar radiation |  | W/m² | 1500 |  |
|  | 3. Currents characteristics |  |  |  |  |
|  | • Maximum temperature rise at In (t° ambient: 45°C) |  |  | Specify |  |
|  | 4. Rated voltage and rated insulation level |  |  |  |  |
|  | • Contact resistance |  | μΩ | Specify |  |
|  | 5. Overload conditions |  |  |  |  |
|  | • Permissible overload currents in accordance with the standard IEC 62271-1 |  |  | Yes |  |
|  | 6. Isolators |  |  |  |  |
|  | • Manufacturer |  |  | Specify |  |
|  | • Type (based IEC) |  |  | Specify |  |
|  | • Height |  | mm | Specify |  |
|  | • Weight |  | kg | Specify |  |
|  | • Number of elements |  |  | 1 |  |
|  | • Used material |  |  | Ceramic |  |
|  | • Profile |  |  | Specify |  |
|  | 7. Operating device |  |  |  |  |
|  | • Type (manufacturer reference) |  |  | Specify |  |
|  | - Three pole operated cabinet |  |  | No |  |
|  | - Single pole operated cabinet |  |  | Yes |  |
|  | - Motorized or manual operated |  |  | motorized |  |
|  | • Motorization |  |  |  |  |
|  | - Rated voltage of the motor |  | Vdc | 220 |  |
|  | - Tolerance |  | % | 85 - 110 |  |
|  | - Capacity |  | W | Specify |  |
|  | - Motor current |  | A | Specify |  |
|  | - Maximum motor current |  | A | Specify |  |
|  | - Rated current for operation at maximum torque |  | A | Specify |  |
|  | - Switching time: |  |  |  |  |
|  | - Closing time of the disconnector |  | s | Specify |  |
|  | - Opening time of the disconnector |  | s | Specify |  |
|  | • Emergency manual operating device available |  |  |  |  |
|  | - Type of operating device (crank,….) |  |  | Specify |  |
|  | - Maximal torque needed for manual opening |  | Nm | Specify |  |
|  | - Maximal torque needed for manual closing |  | Nm | Specify |  |
|  | - Maximal operation height above ground level |  | mm | 1500 |  |
|  | • Number of potential free auxiliary contacts |  |  |  |  |
|  | - Closed – Open - Open: COO |  |  | 4 |  |
|  | - Open – Open - Closed: OOC |  |  | 4 |  |
|  | - Open – Closed - Closed: OCC |  |  | 2 |  |
|  | - Open – Closed - Open: OCO |  |  | 2 |  |
|  | - Breaking capacity |  |  | 4 A at 220 V |  |
|  | - Minimum rated current |  |  | 10 A (class 1) |  |
|  | • Heating |  |  |  |  |
|  | - Rated voltage |  | Vca | 230 |  |
|  | - Tolerance |  | % | 85 - 110 |  |
|  | - Power |  | W | Specify |  |
|  | • Protection level |  |  | ≥IP 55 |  |
|  | 8. Safety and locking |  |  |  |  |
|  | • Normal electrical operated mechanism |  |  |  |  |
|  | - Mechanical locking device placed on motor drive |  |  | Yes |  |
|  | - Motor circuit interrupted by the locking device |  |  | Yes |  |
|  | - Padlockable mechanical locking device in open and closed position (padlocking Ø8mm possible) |  |  | Yes |  |
|  | • Manual drive (if applicable) |  |  | N.A. |  |
|  | - Locking coil in combination with push button |  |  | N.A. |  |
|  | - Supply voltage |  | Vdc | N.A. |  |
|  | - Padlockable mechanical locking device in open and closed position (padlocking Ø8mm possible) |  |  | N.A. |  |
|  | 9. Ergonomics |  |  |  |  |
|  | • Minimum height from ground or circulation level |  |  |  |  |
|  | - bottom skirt of the isolator |  | mm | 2500 |  |
|  | - vertical distance of life part |  | mm | 4500 |  |
|  | • Preferential height from ground or circulation level |  |  |  |  |
|  | - bottom side of the drives |  | mm | 1000 < H < 1600 |  |
|  | - top side of the drives |  | mm | Maximum 2500 |  |
|  | - door handles |  | mm | Maximum 1800 |  |
|  | 10. Mechanical characteristics |  |  |  |  |
|  | • Weight of the complete disconnector |  | kg | Specify |  |
|  | • Weight of the operating mechanism |  |  |  |  |
|  | - Weight of the three pole operating mechanism |  | kg | N.A. |  |
|  | - Weight of the single pole operating mechanism |  | kg | Specify |  |
|  | - Weight of the central control cubicle |  | kg | Specify |  |
|  | 11. Construction details |  |  |  |  |
|  | • Main blades |  |  |  |  |
|  | - Used material for contact (Al, electroplated silver or tinned copper, others) |  |  | Specify |  |
|  | - Contact type |  |  | Specify |  |
|  | - Maximum temperature rise at In (t° ambient: 45°C) |  |  | Specify |  |
|  | - Number of contact fingers |  |  | Specify |  |
|  | - Contact pressure by finger |  | daN | Specify |  |
|  | - Type of electrical connection between elements |  |  | Specify |  |
|  | • HV Terminals |  |  |  |  |
|  | - Diameter (according Inom) |  |  | Specify |  |
|  | - Used material for contact (Al, electroplated silver or tinned copper) |  |  | Specify |  |
|  | - Length |  |  | Specify |  |
|  | - Supply all the parts needed for connecting connection (including connectors on the busbar) |  |  | Yes |  |
|  | 12. Paint and corrosion protection |  |  |  |  |
|  | • Oxydable metal parts |  |  | hot dip galvanizing |  |
|  | • Screws, nuts, bolts,…. |  |  |  |  |
|  | - for diameter ≤ M16 stainless steel |  |  | Yes |  |
|  | - for diameter > M16 hot dip galvanized steel and painted |  |  | Yes |  |
|  | • Frame of control panel galvanized |  |  | Yes |  |
|  | • Duplex principle (galvanized + paint) according GTS |  |  | Yes |  |
|  | • Final color paint |  |  |  |  |
|  | - pieces to earth |  |  | Specify |  |
|  | - live parts |  |  | Specify |  |
|  | - insulator's metal flanges |  |  | Specify |  |
|  | - grounded connections, metallic conductors,… free of paint |  |  |  |  |
|  |  |  |  |  |  |
|  | 13. Documents to be submitted |  |  |  |  |
|  | • Submital fase |  |  | 3 ex. |  |
|  | - General documentation |  |  |  |  |
|  | - List of references |  |  |  |  |
|  | - Type test reports |  |  |  |  |
|  | - datasheet completed |  |  |  |  |
|  | - dimensional drawing |  |  |  |  |
|  | • Ordering fase |  |  | 3 ex. |  |
|  | - operating instruction manual |  |  |  |  |
|  | - erection instruction manual |  |  |  |  |
|  | - maintenance instruction manual |  |  |  |  |
|  | - static and dynamic efforts |  |  |  |  |
|  | - drawings |  |  |  |  |
|  | - detailed dimensional drawing with an indication of weight and efforts |  |  |  |  |
|  | - drawing of the operating cubicle |  |  |  |  |
|  | - drawing of the rating plate |  |  |  |  |
|  | - LV diagrams |  |  |  |  |
|  | - drawing of electrical circuits |  |  |  |  |
|  | - principle diagram of the operating mechanism |  |  |  |  |
|  | • Completed Manufactuer final report including |  |  | 3 ex. |  |
|  | - operating instruction manual |  |  |  |  |
|  | - erection instruction manual |  |  |  |  |
|  | - maintenance instruction manual |  |  |  |  |
|  | - as built drawings and schematics |  |  |  |  |
|  | - factory test report |  |  |  |  |
|  | 14. Languages |  |  |  |  |
|  | • All documents establish in English |  |  | Yes |  |

| TECHNICAL SCHEDULE – Main Data |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Disconnector – 3 Poles - 220kV |  |  |  |  |  |
| Description |  |  | Units | Imposed Values | Guaranteed Values* |
|  | 1. General characteristics |  |  |  |  |
|  | • Manufacturer |  |  | Specify |  |
|  | • Type |  |  | Specify |  |
|  | • Number of poles |  |  | 3 |  |
|  | • Indoor/Outdoor installation |  |  | Outdoor |  |
|  | • Maximum opening time |  | s | 10 |  |
|  | • Maximum closing time |  | s | 10 |  |
|  | • Number of switching events until the first maintenance |  |  | 1000 |  |
|  | • Insulator type |  |  | Brown Porcelain |  |
|  | • Minimum nominal creeping distance |  | mm / kV | 31 |  |
|  | 2. Normal service conditions |  |  |  |  |
|  | • Ambient temperature range |  | °C | -35 to +50 |  |
|  | 3. Currents characteristics |  |  |  |  |
|  | • Main blades |  |  |  |  |
|  | • Rated bay current |  | A | 1600 |  |
|  | • Rated buscoupler current |  | A | 3150 |  |
|  | • Rated short time withstand current |  | kA | 40 |  |
|  | • Rated peak withstand current |  | kA peak | 100 |  |
|  | • Rated duration of short circuit |  | s | 3 |  |
|  | 4. Rated voltage and rated insulation level |  |  |  |  |
|  | • Network nominal voltage |  | kV | 220 |  |
|  | • Rated voltage (Ur) |  | kV | 252 |  |
|  | • Rated frequency |  | Hz | 50 |  |
|  | • Rated duration short-duration power-frequency withstand voltage (Ud) |  |  |  |  |
|  | - Phase to earth |  | kV | 460 |  |
|  | - Across open switching device |  | kV | 530 |  |
|  | • Rated lightning impulse withstand voltage (1,2/50µs) (Up) |  |  |  |  |
|  | - Phase to earth |  | kV peak | 1050 |  |
|  | - Across open switching device |  | kV peak | 1200 |  |
|  | 5. Operating device |  |  |  |  |
|  | • Type of operating device |  |  |  |  |
|  | - Single or three pole operated |  |  | single |  |
|  | - Motorized or manual operated |  |  | motorized |  |
|  | • Motorization |  |  |  |  |
|  | - Rated voltage of the motor |  | Vdc | 220 |  |
|  | • Number of potential free auxiliary contacts |  |  |  |  |
|  | - Closed – Open - Open: COO |  |  | 4 |  |
|  | - Open – Open - Closed: OOC |  |  | 4 |  |
|  | - Open – Closed - Closed: OCC |  |  | 2 |  |
|  | - Open – Closed - Open: OCO |  |  | 2 |  |
|  | • Heating |  |  |  |  |
|  | - Rated voltage |  | Vca | 230 |  |

| TECHNICAL SCHEDULE – Data for Information |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Disconnector – 3 Poles - 220kV |  |  |  |  |  |
| Description |  |  | Units | Imposed Values | Guaranteed Values* |
|  | 1. General characteristics |  |  |  |  |
|  | • Place of manufacture |  |  | Specify |  |
|  | • Standards (latest edition) |  |  | IEC 62271-102 |  |
|  | • Class |  |  |  |  |
|  | - Main blades |  |  | M1 |  |
|  | 2. Normal service conditions(please refer to the site conditions of each substation) |  |  |  |  |
|  | • Ambient temperature range |  | °C |  |  |
|  | • Relative humidity |  | % |  |  |
|  | • Maximum altitude |  | m |  |  |
|  | • Maximum ice coating |  | mm |  |  |
|  | • Maximum pressure of the wind speed |  | Pa |  |  |
|  | • Solar radiation |  | W/m² |  |  |
|  | 3. Currents characteristics |  |  |  |  |
|  | • Maximum temperature rise at In (t° ambient: 45°C) |  |  | Specify |  |
|  | 4. Rated voltage and rated insulation level |  |  |  |  |
|  | • Contact resistance |  | μΩ | Specify |  |
|  | 5. Overload conditions |  |  |  |  |
|  | • Permissible overload currents in accordance with the standard IEC 62271-1 |  |  | Yes |  |
|  | 6. Isolators |  |  |  |  |
|  | • Manufacturer |  |  | Specify |  |
|  | • Type (based IEC) |  |  | Specify |  |
|  | • Height |  | mm | Specify |  |
|  | • Weight |  | kg | Specify |  |
|  | • Number of elements |  |  | 1 |  |
|  | • Used material |  |  | Ceramic |  |
|  | • Profile |  |  | Specify |  |
|  | 7. Operating device |  |  |  |  |
|  | • Type (manufacturer reference) |  |  | Specify |  |
|  | - Three pole operated cabinet |  |  | No |  |
|  | - Single pole operated cabinet (3 cabinets) + 1 central control cubicle |  |  | Yes |  |
|  | - Motorized or manual operated |  |  | motorized |  |
|  | • Motorization |  |  |  |  |
|  | - Rated voltage of the motor |  | Vdc | 220 |  |
|  | - Tolerance |  | % | 85 - 110 |  |
|  | - Capacity |  | W | Specify |  |
|  | - Motor current |  | A | Specify |  |
|  | - Maximum motor current |  | A | Specify |  |
|  | - Rated current for operation at maximum torque |  | A | Specify |  |
|  | - Switching time: |  |  |  |  |
|  | - Closing time of the disconnector |  | s | Specify |  |
|  | - Opening time of the disconnector |  | s | Specify |  |
|  | • Emergency manual operating device available |  |  |  |  |
|  | - Type of operating device (crank,….) |  |  | Specify |  |
|  | - Maximal torque needed for manual opening |  | Nm | Specify |  |
|  | - Maximal torque needed for manual closing |  | Nm | Specify |  |
|  | - Maximal operation height above ground level |  | mm | 1500 |  |
|  | • Number of potential free auxiliary contacts |  |  |  |  |
|  | - Closed – Open - Open: COO |  |  | 4 |  |
|  | - Open – Open - Closed: OOC |  |  | 4 |  |
|  | - Open – Closed - Closed: OCC |  |  | 2 |  |
|  | - Open – Closed - Open: OCO |  |  | 2 |  |
|  | - Breaking capacity |  |  | 4 A at 220 V |  |
|  | - Minimum rated current |  |  | 10 A (class 1) |  |
|  | • Heating |  |  |  |  |
|  | - Rated voltage |  | Vca | 230 |  |
|  | - Tolerance |  | % | 85 - 110 |  |
|  | - Power |  | W | Specify |  |
|  | • Protection level |  |  | ≥IP 55 |  |
|  | 8. Safety and locking |  |  |  |  |
|  | • Normal electrical operated mechanism |  |  |  |  |
|  | - Mechanical locking device placed on motor drive |  |  | Yes |  |
|  | - Motor circuit interrupted by the locking device |  |  | Yes |  |
|  | - Padlockable mechanical locking device in open and closed position (padlocking Ø8mm possible) |  |  | Yes |  |
|  | • Manual drive (if applicable) |  |  | N.A. |  |
|  | - Locking coil in combination with push button |  |  | N.A. |  |
|  | - Supply voltage |  | Vdc | N.A. |  |
|  | - Padlockable mechanical locking device in open and closed position (padlocking Ø8mm possible) |  |  | N.A. |  |
|  | 9. Ergonomics |  |  |  |  |
|  | • Minimum height from ground or circulation level |  |  |  |  |
|  | - bottom skirt of the isolator |  | mm | 2500 |  |
|  | - vertical distance of life part |  | mm | 4500 |  |
|  | • Preferential height from ground or circulation level |  |  |  |  |
|  | - bottom side of the drives |  | mm | 1000 < H < 1600 |  |
|  | - top side of the drives |  | mm | Maximum 2500 |  |
|  | - door handles |  | mm | Maximum 1800 |  |
|  | 10. Mechanical characteristics |  |  |  |  |
|  | • Weight of the complete disconnector |  | kg | Specify |  |
|  | • Weight of the operating mechanism |  |  |  |  |
|  | - Weight of the three pole operating mechanism |  | kg | N.A. |  |
|  | - Weight of the single pole operating mechanism |  | kg | Specify |  |
|  | - Weight of the central control cubicle |  | kg | Specify |  |
|  | 11. Construction details |  |  |  |  |
|  | • Main blades |  |  |  |  |
|  | - Used material for contact (Al, electroplated silver or tinned copper, others) |  |  | Specify |  |
|  | - Contact type |  |  | Specify |  |
|  | - Maximum temperature rise at In (t° ambient: 45°C) |  |  | Specify |  |
|  | - Number of contact fingers |  |  | Specify |  |
|  | - Contact pressure by finger |  | daN | Specify |  |
|  | - Type of electrical connection between elements |  |  | Specify |  |
|  | • HV Terminals |  |  |  |  |
|  | - Diameter (according Inom) |  |  | Specify |  |
|  | - Used material for contact (Al, electroplated silver or tinned copper) |  |  | Specify |  |
|  | - Length |  |  | Specify |  |
|  | - Supply all the parts needed for connecting connection (including connectors on the busbar) |  |  | Yes |  |
|  | 12. Paint and corrosion protection |  |  |  |  |
|  | • Oxydable metal parts |  |  | hot dip galvanizing |  |
|  | • Screws, nuts, bolts,…. |  |  |  |  |
|  | - for diameter ≤ M16 stainless steel |  |  | Yes |  |
|  | - for diameter > M16 hot dip galvanized steel and painted |  |  | Yes |  |
|  | • Frame of control panel galvanized |  |  | Yes |  |
|  | • Duplex principle (galvanized + paint) according GTS |  |  | Yes |  |
|  | • Final color paint |  |  |  |  |
|  | - pieces to earth |  |  | Specify |  |
|  | - live parts |  |  | Specify |  |
|  | - insulator's metal flanges |  |  | Specify |  |
|  | - grounded connections, metallic conductors,… free of paint |  |  |  |  |
|  |  |  |  |  |  |
|  | 13. Documents to be submitted |  |  |  |  |
|  | • Submital fase |  |  | 3 ex. |  |
|  | - General documentation |  |  |  |  |
|  | - List of references |  |  |  |  |
|  | - Type test reports |  |  |  |  |
|  | - datasheet completed |  |  |  |  |
|  | - dimensional drawing |  |  |  |  |
|  | • Ordering fase |  |  | 3 ex. |  |
|  | - operating instruction manual |  |  |  |  |
|  | - erection instruction manual |  |  |  |  |
|  | - maintenance instruction manual |  |  |  |  |
|  | - static and dynamic efforts |  |  |  |  |
|  | - drawings |  |  |  |  |
|  | - detailed dimensional drawing with an indication of weight and efforts |  |  |  |  |
|  | - drawing of the operating cubicle |  |  |  |  |
|  | - drawing of the rating plate |  |  |  |  |
|  | - LV diagrams |  |  |  |  |
|  | - drawing of electrical circuits |  |  |  |  |
|  | - principle diagram of the operating mechanism |  |  |  |  |
|  | • Completed Manufactuer final report including |  |  | 3 ex. |  |
|  | - operating instruction manual |  |  |  |  |
|  | - erection instruction manual |  |  |  |  |
|  | - maintenance instruction manual |  |  |  |  |
|  | - as built drawings and schematics |  |  |  |  |
|  | - factory test report |  |  |  |  |
|  | 14. Languages |  |  |  |  |
|  | • All documents establish in English |  |  | Yes |  |

| TECHNICAL SCHEDULE – Main Data |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Insulating Support - 220kV |  |  |  |  |  |
| Description |  |  | Units | Imposed Values | Guaranteed Values |
|  | 1. General characteristics |  |  |  |  |
|  | • Manufacturer |  |  | Specify |  |
|  | • Type |  |  | Specify |  |
|  | • Installation |  |  | Outdoor |  |
|  | • Rated frequency (fr) |  | Hz | 50 |  |
|  | 2. Normal service conditions |  |  |  |  |
|  | • Ambient temperature range |  | °C | -35 to +50 |  |
|  | 3. Electrical characteristics |  |  |  |  |
|  | • Network nominal voltage |  | kV | 220 |  |
|  | • Maximum service voltage (Um) |  | kV | 245 |  |
|  | - Power frequency withstand voltage 50Hz - 1 min.(Ud) |  | kV | 460 |  |
|  | - Rated operation withstand voltage under rain |  | kV | 750 |  |
|  | - Lightning Impulse withstand voltage (1,2/50µs) |  | kV | 1050 |  |
|  | 4. Characteristics of insulating support |  |  |  |  |
|  | • Housing (porcelain, polymer) |  |  | Porcelain - Brown |  |
|  | • Minimum phase creepage distance |  | mm/kV | 31 |  |

| TECHNICAL SCHEDULE – Data for Information |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Insulating Support - 220kV |  |  |  |  |  |
| Description |  |  | Units | Imposed Values | Guaranteed Values |
|  | 1. General characteristics |  |  |  |  |
|  | •Place of manufacture |  |  | Specify |  |
|  | • Standards |  |  | IEC 60273 |  |
|  | 2. Normal service conditions(please refer to the site conditions of each substation) |  |  |  |  |
|  | • Ambient temperature range |  | °C |  |  |
|  | • Relative humidity |  | % |  |  |
|  | • Maximum altitude |  | m |  |  |
|  | • Maximum ice coating |  | mm |  |  |
|  | • Maximum pressure of the wind speed |  | Pa |  |  |
|  | • Solar radiation |  | W/m² |  |  |
|  | 3. Mechanical characteristics |  |  |  |  |
|  | • Flexion |  |  |  |  |
|  | -breaking load |  | N | Specify |  |
|  | -permissible continuous effort on top without damage |  | % | Specify |  |
|  | -permissible effort on top on short circuit without damage |  | % | Specify |  |
|  | -duration |  | s | Specify |  |
|  | • Torsion: breaking load |  | Nm | Specify |  |
|  | • Strength: breaking load |  | N | Specify |  |
|  | • Compression: breaking load |  | N | Specify |  |
|  | 4. Characteristics of insulating support |  |  |  |  |
|  | • Mounting |  |  | standing or hanging |  |
|  | • Housing (porcelain, polymer) |  |  | porcelain |  |
|  | • Number of elementary columns |  |  | Specify |  |
|  | • Total height of the insulating support |  | mm | Specify |  |
|  | • Fixations |  |  |  |  |
|  | -top (voltage side) |  |  |  |  |
|  | -circle diameter of fixation |  | mm | Specify |  |
|  | -number of screws |  |  | Specify |  |
|  | -drillings for screws |  |  | Specify |  |
|  | -base (earth side) |  |  |  |  |
|  | -circle diameter of fixation |  | mm | Specify |  |
|  | -number of screws |  |  | Specify |  |
|  | -drillings for screws |  |  | Specify |  |
|  | • Weight |  | kg | Specify |  |
|  | 5. Paint and corrosion protection |  |  |  |  |
|  | • Oxydable metal parts |  |  | hot dip galvanizing |  |
|  | • Screws, nuts, bolts,…. |  |  |  |  |
|  | - for diameter ≤ M16 stainless steel |  |  | Yes |  |
|  | - for diameter > M16 hot dip galvanized steel and painted |  |  | Yes |  |
|  | • Duplex principle (galvanized + paint) according GTS |  |  | Yes |  |
|  | • Final color paint |  |  |  |  |
|  | - pieces to earth |  |  | Specify |  |
|  | - live parts |  |  | Specify |  |
|  | - insulator's metal flanges |  |  | Specify |  |
|  | - grounded connections, metallic conductors,… free of paint |  |  |  |  |
|  |  |  |  |  |  |
|  | 6. Documents to be submitted |  |  |  |  |
|  | • Submital fase |  |  | 3 ex. |  |
|  | - General documentation |  |  |  |  |
|  | - datasheet completed |  |  |  |  |
|  | - dimensional drawing |  |  |  |  |
|  | • Ordering fase |  |  | 3 ex. |  |
|  | - erection instruction manual |  |  |  |  |
|  | - maintenance instruction manual |  |  |  |  |
|  | - static and dynamic efforts |  |  |  |  |
|  | - dimensional drawing |  |  |  |  |
|  | • Completed Manufactuer final report including |  |  | 3 ex. |  |
|  | - erection instruction manual |  |  |  |  |
|  | - maintenance instruction manual |  |  |  |  |
|  | - as built drawing |  |  |  |  |
|  | 7. Languages |  |  |  |  |
|  | • All documents establish in English |  |  | Yes |  |

| TECHNICAL SCHEDULE – Main Data |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Phase Surge Arrester - 220kV |  |  |  |  |  |
| Description |  |  | Units | Imposed Values | Guaranteed Values |
|  | 1. General characteristics |  |  |  |  |
|  | • Manufacturer |  |  | Specify |  |
|  | • Type |  |  | Specify |  |
|  | • Installation |  |  | Outdoor |  |
|  | • Housing |  |  | Porcelain - Brown |  |
|  | • Minimum phase creepage distance |  | mm/kV | 31 |  |
|  | 2. Normal service conditions |  |  |  |  |
|  | • Ambient temperature range |  | °C | -35 to +50 |  |
|  | 3. Electrical characteristics |  |  |  |  |
|  | • Rated frequency (fr) |  | Hz | 50 |  |
|  | • Network nominal voltage |  | kV | 220 |  |
|  | • Maximum service voltage (Um) |  | kV | 245 |  |
|  | • Nominal discharge current |  | kA peak | 10 |  |
|  | • Continuous Operating Voltage (Uc - COV) |  | kV | 152 |  |
|  | • Insulation level for the housing |  |  |  |  |
|  | - Power frequency withstand voltage 50Hz - 1 min. |  | kV | 460 |  |
|  | - Lightning Impulse withstand voltage (1,2/50µs) |  | kV | 1050 |  |

| TECHNICAL SCHEDULE – Data for Information |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Phase Surge Arrester - 220kV |  |  |  |  |  |
| Description |  |  | Units | Imposed Values | Guaranteed Values |
|  | 1. General characteristics |  |  |  |  |
|  | • Manufacturer |  |  | Specify |  |
|  | • Standards |  |  | IEC |  |
|  | • Construction type |  |  | MO (metal oxide) |  |
|  | • Model |  |  | Specify |  |
|  | • Surge counter |  |  | Yes |  |
|  | -number |  |  | 1 by phase |  |
|  | -type |  |  | Specify |  |
|  | 2. Normal service conditions(please refer to the site conditions of each substation) |  |  |  |  |
|  | • Ambient temperature range |  | °C |  |  |
|  | • Relative humidity |  | % |  |  |
|  | • Maximum altitude |  | m |  |  |
|  | • Maximum ice coating |  | mm |  |  |
|  | • Maximum pressure of the wind speed |  | Pa |  |  |
|  | • Solar radiation |  | W/m² |  |  |
|  | 3. Electrical characteristics |  |  |  |  |
|  | • Surge arrester rated voltage (Ur) |  | kV | Specify |  |
|  | • Maximum temporary Over Voltage |  |  |  |  |
|  | - for 1 s |  | kV | Specify |  |
|  | - for 10 s |  | kV | Specify |  |
|  | • Maximum residual voltages for a lightning impulse 8/20 μs |  |  |  |  |
|  | - at I = 5 kA |  | kV peak | Specify |  |
|  | - at I = 10 kA |  | kV peak | Specify |  |
|  | - at I = 20 kA |  | kV peak | Specify |  |
|  | • Maximum residual voltages for a lightning impulse 30/... μs |  |  |  |  |
|  | - at I = 1 kA |  | kV peak | Specify |  |
|  | • Line discharge class (IEC 60099-4) |  |  | Specify |  |
|  | • Reference current and voltage |  | kV /mA | Specify |  |
|  | 4. Mechanical characteristics |  |  |  |  |
|  | • Pollution Class |  |  | outstanding (no pollution) |  |
|  | • Over-pressure valve |  |  | Yes/No |  |
|  | - type |  |  | Specify |  |
|  | - pressure relief capability |  | kA | ≥31,5 |  |
|  | • Maximum allowed strength (MPSL) |  | N | Specify |  |
|  | • Maximum dynamic allowed strength (MPDSL) |  | N | Specify |  |
|  | • Total height (including insulated base) |  | mm | Specify |  |
|  | • Total weight |  | kg | Specify |  |
|  | 5. Contruction details |  |  |  |  |
|  | • Type of line connection (Al, ...) |  |  | Specify |  |
|  | • Type of ground connection ( stainless steel, ….) |  |  | Specify |  |
|  | • Insulated base |  |  | Yes |  |
|  | • Guard ring (outer diameter) |  | mm | Specify |  |
|  | • Number of elementary columns |  |  | Specify |  |
|  | • Terminal for connection of online Leakage Current Measurement system |  |  | Yes |  |
|  | 6. Paint and corrosion protection |  |  |  |  |
|  | • Oxydable metal parts |  |  | hot dip galvanizing |  |
|  | • Screws, nuts, bolts,…. |  |  |  |  |
|  | - for diameter ≤ M16 stainless steel |  |  | Yes |  |
|  | - for diameter > M16 hot dip galvanized steel and painted |  |  | Yes |  |
|  | • Duplex principle (galvanized + paint) according GTS |  |  | Yes |  |
|  | • Final color paint |  |  |  |  |
|  | - pieces to earth |  |  | Specify |  |
|  | - live parts |  |  | Specify |  |
|  |  |  |  |  |  |
|  | 7. Testing |  |  |  |  |
|  | • Reports of type tests on similar equipment |  |  | Yes |  |
|  | • Routine test according to IEC 60099.4 |  |  | Yes |  |
|  | 8. Documents to be submitted |  |  |  |  |
|  | • Submital fase |  |  | 3 ex. |  |
|  | - General documentation |  |  |  |  |
|  | - List of references |  |  |  |  |
|  | - Type test reports |  |  |  |  |
|  | - datasheet completed |  |  |  |  |
|  | - dimensional drawing |  |  |  |  |
|  | • Ordering fase |  |  | 3 ex. |  |
|  | - erection instruction manual |  |  |  |  |
|  | - maintenance instruction manual |  |  |  |  |
|  | - static and dynamic efforts |  |  |  |  |
|  | - voltage curve at power-frequency in function of time |  |  |  |  |
|  | - drawings |  |  |  |  |
|  | - detailed dimensional drawing |  |  |  |  |
|  | - drawing of the rating plate |  |  |  |  |
|  | • Completed Manufactuer final report including |  |  | 3 ex. |  |
|  | - erection instruction manual |  |  |  |  |
|  | - maintenance instruction manual |  |  |  |  |
|  | - as built drawings |  |  |  |  |
|  | - voltage curve at power-frequency in function of time |  |  |  |  |
|  | - factory test report |  |  |  |  |
|  | 9. Languages |  |  |  |  |
|  | • All documents establish in English |  |  | Yes |  |

| TECHNICAL SCHEDULE – Main Data Capacitive Voltage Transformer 220kV |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Description |  |  | Units | Imposed Values | Guaranteed Values |
|  | 1. General characteristics |  |  |  |  |
|  | • Manufacturer |  |  | Specify |  |
|  | • Type |  |  | Single phase Oil Immersed Capacitive |  |
|  | • Indoor/Outdoor installation |  |  | Outdoor |  |
|  | • Insulator type |  |  | Brown Procelain |  |
|  | • Minimum nominal creeping distance |  | mm / kV | 31 |  |
|  | 2. Normal service conditions |  |  |  |  |
|  | • Ambient temperature range |  | °C | -35 to +50 |  |
|  | 3. Electrical characteristics |  |  |  |  |
|  | • Service voltage |  | kV | 220 |  |
|  | • Rated frequency (fr) |  | Hz | 50 |  |
|  | • Rated voltage (Ur) |  | kV | 252 |  |
|  | • Rated short duration power-frequency withstand voltage (AC) 1min-50Hz (Ud) |  | kV | 460 |  |
|  | • Rated lightning impulse withstand voltage (Up) |  | kV peak | 1050 |  |
|  | 4. Windings characteristics |  |  |  |  |
|  | • Rated primary voltage |  | kV eff | 220/√3 |  |
|  | • Voltage factors |  |  |  |  |
|  | - 1.2 Un - permanent |  |  | Yes |  |
|  | - 1.9 Un - 8 hours |  |  | Yes |  |
|  | • Secondary windings |  |  |  |  |
|  | - number |  |  | 3 |  |
|  | • Rated secondary voltage |  |  |  |  |
|  | - Winding nr.1 (metering) |  | V | 100/√3 |  |
|  | - Winding nr.2 (measuring) |  | V | 100/√3 |  |
|  | - Winding nr.3 (ptotection) |  | V | 100/√3 |  |
|  | • Accuracy class |  |  |  |  |
|  | - Winding nr.1 (metering) |  | cl. | 0.2 |  |
|  | - Winding nr.2 (measuring) |  | cl. | 0.5 |  |
|  | - Winding nr.3 (ptotection) |  | cl. | 3P |  |
|  | • Accuracy burden |  |  |  |  |
|  | - Winding nr.1 (metering) |  | VA | 50 |  |
|  | - Winding nr.2 (measuring) |  | VA | 200 |  |
|  | - Winding nr.3 (ptotection) |  | VA | 200 |  |
|  | • Temperature rise limit (secondary) |  | VA | Specify |  |
|  | • Secondary windings |  |  |  |  |
|  | - Short duration power-frequency withstand voltage (AC) 1min-50Hz |  | kV | 3 |  |
|  | • Rated frequency range (% fr) |  |  |  |  |
|  | - cl.0.2 |  | % | 99 to 101 |  |
|  | - cl.0.5 |  | % | 99 to 101 |  |
|  | - 3P |  | % | 96 to 102 |  |

| TECHNICAL SCHEDULE – Data for Information Capacitive Voltage Transformer 220kV |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Description |  |  | Units | Imposed Values | Guaranteed Values |
|  | 1. General characteristics |  |  |  |  |
|  | • Place of manufacture |  |  | Specify |  |
|  | • Type |  |  | Specify |  |
|  | • Standards (latest edition) |  |  | IEC 61869-1/5 IEC 60358-1/2 |  |
|  | • Planned for line trap mounting |  |  | Yes |  |
|  | • High frequency output terminal for HF signal transmission |  |  | Yes |  |
|  | • Completely sealed construction |  |  | Specify |  |
|  | • Hermeticity type system |  |  | Specify |  |
|  | 2. Normal service conditions(please refer to the site conditions of each substation) |  |  |  |  |
|  | • Ambient temperature range |  | °C |  |  |
|  | • Relative humidity |  | % |  |  |
|  | • Maximum altitude |  | m |  |  |
|  | • Maximum ice coating |  | mm |  |  |
|  | • Maximum pressure of the wind speed |  | Pa |  |  |
|  | • Solar radiation |  | W/m² |  |  |
|  | 3. Capacitors Values |  |  |  |  |
|  | • Capacity of the HV capacitor (upper) capacitor C1 |  | pF | Specify |  |
|  | • Capacity of intermediate capacitor (lower) C2 |  | pF | Specify |  |
|  | CN=C1.C2C1+C2 • Rated Capacity. |  | pF | à spécifier |  |
|  | • Tolerances on rated capacity |  | % | -5 à 10 |  |
|  | 4. Capacitors characteristics. |  |  |  |  |
|  | • Tangent δ or loss angle of the capacitor |  |  |  |  |
|  | - at 20°C and 50Hz, between 0.1 and 1.5 x Ur,p (225/√3kV) |  |  | < 0.005 |  |
|  | - maximum variation at Ur,p (225/√3kV) and between +5°C and 50°C after 12 months in service |  |  | ≤ 0.001 |  |
|  | • maximum temperature coefficient of the capacitor |  | % / °C | < 0.1 |  |
|  | • capacitors stability coefficient (after 12 months in service) |  | % | 1 |  |
|  | • Capacitor voltage gradient at Ur/√3 |  | kV/mm | Specify |  |
|  | 5. Additional conditions for HF signal transmission |  |  |  |  |
|  | • Apparent capacity for frequencies between 40 to 400kHz |  | pF | 5000 |  |
|  | - maximum variations |  | % | -12% / 20% |  |
|  | - parasitic capacitance of the LV terminal |  | pF | < 500 |  |
|  | - parasitic conductance of the LV terminal |  | µS | < 50 |  |
|  | - equivalent series resistance for frequencies between 40 to 400kHz |  | Ω | < 40 |  |
|  | 6. Insulation characteritics |  |  |  |  |
|  | Capacitive units |  |  | Specify |  |
|  | • Internal insulation |  |  | Specify |  |
|  | • Oil |  |  |  |  |
|  | - type |  |  | Specify |  |
|  | - supplier and oil reference |  |  | Specify |  |
|  | Electromagnetic unit |  |  | Specify |  |
|  | • Internal insulation |  |  | Specify |  |
|  | • Oil |  |  |  |  |
|  | - type |  |  | Specify |  |
|  | - supplier and oil reference |  |  | Specify |  |
|  | External insulation |  |  |  |  |
|  | • Manufacturer |  |  | Specify |  |
|  | • Number of elements |  |  | 1 |  |
|  | 7. Mechanical characteristics |  |  |  |  |
|  | • Total height |  | mm | Specify |  |
|  | • Total weight |  | kg | Specify |  |
|  | • Primary terminals |  |  |  |  |
|  | - alloy |  |  | Tinned copper |  |
|  | - diameter |  | mm | Specify |  |
|  | - Contact length |  | mm | Specify |  |
|  | - Height (axis ground surface - primary terminal) |  | mm | Specify |  |
|  | • Capacitive units |  |  |  |  |
|  | - total weight |  | kg | Specify |  |
|  | - oil weight |  | kg | Specify |  |
|  | • Electromagnetic unit |  |  |  |  |
|  | - total weight |  | kg | Specify |  |
|  | - oil weight |  | kg | Specify |  |
|  | • Transportation weight |  |  |  |  |
|  | - Capacitor C1 |  | kg | Specify |  |
|  | - Capacitor C2 |  | kg | Specify |  |
|  | 8. Paint and corrosion protection |  |  |  |  |
|  | • Oxydable metal parts |  |  | hot dip galvanizing |  |
|  | • Screws, nuts, bolts,…. |  |  |  |  |
|  | - for diameter ≤ M16 stainless steel |  |  | Yes |  |
|  | - for diameter > M16 hot dip galvanized steel and painted |  |  | Yes |  |
|  | • Frame of control panel galvanized |  |  | Yes |  |
|  | • Duplex principle (galvanized + paint) according GTS |  |  | Yes |  |
|  | • Final color paint |  |  |  |  |
|  | - pieces to earth |  |  | Specify |  |
|  | - live parts |  |  | Specify |  |
|  | - insulator's metal flanges |  |  | Specify |  |
|  | - grounded connections, metallic conductors,… free of paint |  |  |  |  |
|  |  |  |  |  |  |
|  | 9. Documents to be submitted |  |  |  |  |
|  | • Submital fase |  |  | 3 ex. |  |
|  | - General documentation |  |  |  |  |
|  | - List of references |  |  |  |  |
|  | - Type test reports |  |  |  |  |
|  | - datasheet completed |  |  |  |  |
|  | - dimensional drawing |  |  |  |  |
|  | • Ordering fase |  |  | 3 ex. |  |
|  | - erection instruction manual |  |  |  |  |
|  | - maintenance instruction manual |  |  |  |  |
|  | - static and dynamic efforts |  |  |  |  |
|  | - detailed description of the air-oil hermeticity system |  |  |  |  |
|  | - drawings |  |  |  |  |
|  | - detailed dimensional drawing |  |  |  |  |
|  | - dimensional drawing of the Capacitors |  |  |  |  |
|  | - dimensional drawing of the electromagnetic unit |  |  |  |  |
|  | - drawing of the LV terminals cabinet |  |  |  |  |
|  | - drawing of the rating plate |  |  |  |  |
|  | • Completed Manufactuer final report including |  |  | 3 ex. |  |
|  | - erection instruction manual |  |  |  |  |
|  | - maintenance instruction manual |  |  |  |  |
|  | - as built drawings and schematics |  |  |  |  |
|  | - factory test report |  |  |  |  |
|  | 10. Languages |  |  |  |  |
|  | • All documents establish in English |  |  | Yes |  |

| TECHNICAL SCHEDULE – Main Data AutoTransformer 220/110/10 kV 63MVA |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Description |  |  | Units | Imposed Values | Guaranteed Values |
|  | 1. General characteristics |  |  |  |  |
|  | • Manufacturer |  |  | Specify |  |
|  | • Oil immersed three-phase transformer |  |  | Yes |  |
|  | • Type (Core or Shell) |  |  | Core |  |
|  | • Indoor/Outdoor installation |  |  | Outdoor |  |
|  | • Frequency |  | Hz | 50 |  |
|  | • Number of windings per phase |  |  | 3 |  |
|  | 2. Normal service conditions |  |  |  |  |
|  | • Ambient temperature range |  | °C | -35 to +50 |  |
|  | 3. Rated power, temperature rise and overload |  |  |  |  |
|  | • Cooling mode |  |  | ONAN / ONAF1 / ONAF2 |  |
|  | • Rated power |  |  |  |  |
|  | - primary windings (220kV) |  | MVA | 42 / 52.5 / 63 |  |
|  | - secondary windings (110kV) |  | MVA | 42 / 52,5 / 63 |  |
|  | - tertiary windings (10kV) |  | MVA | 20 / 30 / 40 |  |
|  | 4. Rated voltages levels |  |  |  |  |
|  | Service Voltages (Un) |  |  |  |  |
|  | - Primary windings |  | kV | 220 |  |
|  | - Secondary windings |  | kV | 110 |  |
|  | - Tertiary windings |  | kV | 10 |  |
|  | Rated Voltages (Ur) |  |  |  |  |
|  | - Primary windings |  | kV | 252 |  |
|  | - Secondary windings |  | kV | 126 |  |
|  | - Tertiary windings |  | kV | 12 |  |
|  | 5. Insulation levels according IEC |  |  |  |  |
|  | • Rated short duration power-frequency withstand voltage (AC) 1min-50Hz (Ud) |  |  |  |  |
|  | - Primary windings |  | kV | 460 |  |
|  | - Secondary windings |  | kV | 230 |  |
|  | - Tertiary windings |  | kV | 28 |  |
|  | • Rated lightning impulse withstand voltage (1,2/50µs) (Up) |  |  |  |  |
|  | - Primary windings |  | kVpeak | 1050 |  |
|  | - Secondary windings |  | kVpeak | 550 |  |
|  | - Tertiary windings |  | kVpeak | 75 |  |
|  | 6. Vector group |  |  | YN,yn0,d11 |  |
|  | 7. Voltage and current characteristics |  |  |  |  |
|  | • Voltage ratio |  | kV | 220/110/10 |  |
|  | • Tapping range on HV side |  | % | ± 10 x1,5% |  |
|  | • Number of taps |  |  | 21 |  |
|  | - Tap nr. 1 (highest ratio) |  | kV | 253 |  |
|  | - Tap nr. 11 (principal tap) |  | kV | 220 |  |
|  | - Tap nr. 21 (lowest ratio) |  | kV | 187 |  |
|  | 8. Losses |  |  |  |  |
|  | • No load loss at rated voltage and frequency (P1) |  |  |  |  |
|  | - Value |  | kW | ≤ 25 |  |
|  |  25 luead loss at rated voltage and frequency (P1)0µs) (Up)C) 1 min-50Hz (Ud)onths in service)e)rthin energy l |  |  |  |  |
|  | - Tap nr. 11 (principal tap) (P2) |  |  |  |  |
|  | . load loss |  | kW | ≤ 120 |  |
|  | 9. Short-circuit impedance |  |  |  |  |
|  | • Short circuit impedance at the rated power of 63 MVA for all the taps of the OLTC |  |  | HV-MV |  |
|  | - Primary / Secondary |  | % | 12 |  |
|  | - Primary / Tertiary |  | % | 10 |  |
|  | - Secondary / Tertiary |  | % | Specify |  |
|  | -Tolerances (on measured values) |  | % | according IEC |  |
|  | 10. Sound level |  |  |  |  |
|  | • Sound level guaranteed and measured according to IEC 60076-10 at principal tap, rated induction and frequency (ONAF) |  | dB(A) | ≤ 72 |  |

| TECHNICAL SCHEDULE – Data for Information AutoTransformer 220/110/10 kV 63MVA |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Description |  |  | Units | Imposed Values | Guaranteed Values |
|  | 1. General characteristics |  |  |  |  |
|  | • Place of manufacture |  |  | Specify |  |
|  | • Standards (latest edition) |  |  | IEC 60076 |  |
|  | • Internal insulation paper and oil |  |  | Yes |  |
|  | • Cooling radiators air / oil fixed on the tank |  |  | Yes |  |
|  | • Oil conservator mounted on the tank |  |  | Yes |  |
|  | 2. Normal service conditions(please refer to the site conditions of each substation) |  |  |  |  |
|  | • Ambient temperature range |  | °C |  |  |
|  | • Relative humidity |  | % |  |  |
|  | • Maximum altitude |  | m |  |  |
|  | • Maximum ice coating |  | mm |  |  |
|  | • Maximum pressure of the wind speed |  | Pa |  |  |
|  | • Solar radiation |  | W/m² |  |  |
|  | 3. Rated power, temperature rise and overload |  |  |  |  |
|  | • Particular operating conditions |  |  |  |  |
|  | - rated power must be considered with the following independent or simultaneous parameter changes: |  |  |  |  |
|  | - variations of the operating voltage (max./min.) |  | kV | 245/205 |  |
|  | - variations of the frequency |  | Hz | 50 +/- 0.5 |  |
|  | • Maximum temperature rise at rated power for all taps and cooling modes |  |  |  |  |
|  | - Top oil temperature rise (by thermometer measurement) |  | K | 60 |  |
|  | - B57 (by temperature probes) |  | K | 65 |  |
|  | - Winding "hot spot" temperature rise |  | K | 78 |  |
|  | - Secondary windings |  | kVpeak | 550 |  |
|  | - Tertiary windings |  | kVpeak | 75 |  |
|  | 4. Voltage and current characteristics |  |  |  |  |
|  | • Primary nominal current |  | A | Specify |  |
|  | • Secondary nominal current |  | A | Specify |  |
|  | • Tertiary nominal current |  | A | Specify |  |
|  | 5. Tap changer (OLTC) |  |  |  |  |
|  | • Manufacturer |  |  | Specify |  |
|  | • Type: Reinhausen (MR) vaccum type (VACUTAP) or equivalent |  |  | Yes |  |
|  | • Location |  |  |  |  |
|  | - Neutral HV bushing |  |  | NO |  |
|  | - on primary winding |  |  | Yes |  |
|  | • Number of positions |  |  | 21 |  |
|  | • The OLTC supports permanently 120 % of the highest rated current of the transformer |  |  | Specify |  |
|  | • Tapping range |  | % | ± 10 x1,5% |  |
|  | • Rated current |  | A | Specify |  |
|  | • maximum voltage between two successive taps corresponding to In |  | kV | Specify |  |
|  | • Number of switch cycles without maintenance |  |  |  |  |
|  | - At the highest rated current of the transformer |  |  | Specify |  |
|  | - At 1.5 x the highest rated current of the transformer |  |  | Specify |  |
|  | • switching time between two successive taps |  | s | Specify |  |
|  | • transition impedance from resistive-type |  |  | Specify |  |
|  | • Motor drive unit |  |  |  |  |
|  | - Type |  |  | Specify |  |
|  | - Rated supply voltage of the motor |  |  | Specify |  |
|  | 6. Losses |  |  |  |  |
|  | • No load loss at rated voltage and frequency (P1) |  |  |  |  |
|  | - Tolerances |  | % | + 15 |  |
|  |  15lerancesss at rated voltage and frequency (P1)ormerding to Int of the transformereter changes:and frequen |  |  |  |  |
|  | - Tap nr. 1 |  |  |  |  |
|  | . load loss |  | kW | Specify |  |
|  | . Tolerances |  | % | + 15 |  |
|  | - Tap nr. 11 (principal tap) (P2) |  |  |  |  |
|  | . Tolerances |  | % | + 15 |  |
|  | - Tap nr. 21 |  |  |  |  |
|  | . load loss |  | kW | Specify |  |
|  | . Tolerances |  | % | + 15 |  |
|  | - Total losses (P1 + P2) |  |  |  |  |
|  | . load loss |  | kW | Specify |  |
|  | . Tolerances |  | % | + 10 |  |
|  | • Power taken by cooling equipment (P3) |  |  |  |  |
|  | . Value |  | kW | Specify |  |
|  | 7. Magnetic characteristics |  |  |  |  |
|  | • Permanent over-voltage |  | % | Specify |  |
|  | • Short time duration over-voltage - 3 hours |  | % | Specify |  |
|  | • Magnetic steel: quality |  |  | Specify |  |
|  | - Type of core |  |  | Specify |  |
|  | • Rated induction at rated voltage and frequency. |  | T | Specify |  |
|  | • No-load current (Io) at rated voltage and frequency |  | A | Specify |  |
|  | - No-load current: tolerances |  | % | Specify |  |
|  | • Specific losses of magnetic steel |  | kW | Specify |  |
|  | - Tolerances |  | % | Specify |  |
|  | 8. Overload capabilities |  |  |  |  |
|  | • Overload conditions: subsequent at operating at rated power, average ambient temperature of 40 ° C, hot spot windings temperature limited to 115 ° C |  |  |  |  |
|  | - Overload duration at 120% |  | min | Specify |  |
|  | - Overload duration at 200% |  | min | Specify |  |
|  | • Time constant temperature rises |  |  |  |  |
|  | - Top oil temperature rise |  | h | Specify |  |
|  | - Average winding temperature rise |  | min | Specify |  |
|  | 9. Exceptional service conditions |  |  |  |  |
|  | • Short-circuit withstand capability of the windings ( for every position of the OLTC) |  |  | Yes |  |
|  | - Short-circuit power of the network |  | kA | 31.5 |  |
|  | - Maximum short-circuit duration (max. Voltage applied, acc. IEC 60909) |  | s | 1 |  |
|  | • direct Impedance / the zero sequence impedance is between 1 and 3 |  |  | Yes |  |
|  | • Maximum allowed value of the average temperature of the windings corresponding, starting from a average temperature of 105 ° C (50 ° C + 55 ° C) |  |  | Specify |  |
|  | 10. Current transformers |  |  |  |  |
|  | • For winding temperature (thermal image) |  |  | Yes |  |
|  | - can be short-circuited in the control cubicle |  |  | Yes |  |
|  | • For other purposes |  |  | No |  |
|  | • Distribution of cores |  |  |  |  |
|  | - side 220kV (phase and neutral) |  |  | N.A. |  |
|  | - side 110kV (phase and neutral) |  |  | N.A. |  |
|  | - side 10kV (phase) |  |  | N.A. |  |
|  | 11. Construction characteristics |  |  |  |  |
|  | Windings |  |  |  |  |
|  | • type of winding line side |  |  | Specify |  |
|  | • Relative position of the windings compared to the magnetic core |  |  | Specify |  |
|  | Cooling |  |  |  |  |
|  | • Cooling mode |  |  | ONAN/ONAF 1/ONAF 2 |  |
|  | • Fans characteristics |  |  | Specify |  |
|  | - Number |  |  | Specify |  |
|  | - Rated power according to IEC standards, within the limits of heating guarantees with coolers |  | MVA | Specify |  |
|  | - Manufacturer |  |  | Specify |  |
|  | - Nature, galvanized steel plates, others |  |  | Specify |  |
|  | • Fans characteristics |  |  |  |  |
|  | - Manufacturer |  |  | Specify |  |
|  | - Type |  |  | Specify |  |
|  | - Number |  |  | Specify |  |
|  | - Power consumption |  | kW | Specify |  |
|  | - Speed |  | rpm | Specify |  |
|  | • Oil conservator |  |  | Yes |  |
|  | - Mounted on the tank on a metal frame |  |  | Yes |  |
|  | - Two separate compartments (transformer and switch of the OLTC) |  |  | Yes |  |
|  | - With rubber expansion membrane (transformer part) |  |  | Yes |  |
|  | - Vacuum filter through and dryer regenerable hygroscopic salts |  |  | Yes |  |
|  | - Maximum allowable over-pressure |  | kPa | 2 |  |
|  | - With filling plug |  |  | Yes |  |
|  | • Tank |  |  |  |  |
|  | - Welded or bolted cover |  |  | Specify |  |
|  | - Allowable over-pressure on cover level |  | kPa | 35 |  |
|  | - Allowable over-pressure on the tank |  | kPa | 2 |  |
|  | - Pressure relief valve (Qualitrol type) |  |  | Yes |  |
|  | - Wheels capable of being directed in two perpendicular directions: |  |  |  |  |
|  | - Number |  |  | 4 |  |
|  | - Inner distances between rails |  |  | Specify |  |
|  | . transversal axle |  | mm | / |  |
|  | . longitudinal axle |  | mm |  |  |
|  | - wheel blocking systems included |  |  |  |  |
|  | • Bushings |  |  |  |  |
|  | • Primary H.V. 220kV (phase) |  |  |  |  |
|  | - Number |  |  | 3 |  |
|  | - Manufacturer |  |  | Specify |  |
|  | - Nature of the internal insulation |  |  | Specify |  |
|  | - Oil - paper |  |  |  |  |
|  | - synthetic resin and paper |  |  |  |  |
|  | • Rated voltage (Ur) |  | kV | 245 |  |
|  | • Rated lightning impulse withstand voltage (Up) |  | kV peak | 1050 |  |
|  | • Rated current (minimum = 120% I rated transformer) |  | A | Specify |  |
|  | - Dry arcing distance |  | mm | Specify |  |
|  | - Developed creepage distance |  | mm/kV | 31 |  |
|  | - Space for bushing CT |  |  | N.A. |  |
|  | • H.V. 220kV (neutral) |  |  |  |  |
|  | - Number |  |  | 1 |  |
|  | - Manufacturer |  |  | Specify |  |
|  | - Nature of the internal insulation |  |  | Specify |  |
|  | - Oil - paper |  |  |  |  |
|  | - synthetic resin and paper |  |  |  |  |
|  | • Rated voltage (Ur) |  | kV | 245 |  |
|  | • Rated lightning impulse withstand voltage (Up) |  | kV peak | 1050 |  |
|  | • Rated current (minimum = 120% I rated transformer) |  | A | Specify |  |
|  | - Dry arcing distance |  | mm | Specify |  |
|  | - Developed creepage distance |  | mm/kV | 31 |  |
|  | - Space for bushing CT |  |  | N.A. |  |
|  | • Secondary H.V. 110kV (phase and neutral) |  |  |  |  |
|  | - Number |  |  | 4 |  |
|  | - Manufacturer |  |  | Specify |  |
|  | - Nature of the internal insulation |  |  | Specify |  |
|  | - Oil - paper |  |  |  |  |
|  | - synthetic resin and paper |  |  |  |  |
|  | • Rated voltage (Ur) |  | kV | 123 |  |
|  | • Rated lightning impulse withstand voltage (Up) |  | kV peak | 550 |  |
|  | • Rated current (minimum = 120% I rated transformer) |  | A | Specify |  |
|  | - Dry arcing distance |  | mm | Specify |  |
|  | - Developed creepage distance |  | mm/kV | 31 |  |
|  | - Space for bushing CT |  |  | N.A. |  |
|  | • Tertiary M.V. 10kV (phase) |  |  |  |  |
|  | - Number |  |  | 3 |  |
|  | - Manufacturer |  |  | Specify |  |
|  | - Nature of the internal insulation |  |  | Specify |  |
|  | - Oil - paper |  |  |  |  |
|  | - synthetic resin and paper |  |  |  |  |
|  | • Rated voltage (Ur) |  | kV | 12 |  |
|  | • Rated lightning impulse withstand voltage (Up) |  | kV peak | 75 |  |
|  | • Rated current (minimum = 120% I rated transformer) |  | A | Specify |  |
|  | - Dry arcing distance |  | mm | Specify |  |
|  | - Developed creepage distance |  | mm/kV | 31 |  |
|  | - Space for bushing CT |  |  | N.A. |  |
|  | 12. Oil |  |  |  |  |
|  | • Oil manufacturer |  |  | Specify |  |
|  | • Oil type (Nynas Nitro or equivalent without PCB, unsulfided and with inhibitor) |  |  | Specify |  |
|  | • Oil with inhibitor |  |  | Yes |  |
|  | - Manufacturer |  |  | Specify |  |
|  | - Type |  |  | Specify |  |
|  | • Conform with IEC 60.296 |  |  | Yes |  |
|  | • The specified oil will be of a non corrosive type. Corrosivity will be checked in accordance to the latest CIGRE recommendations (WG A2-32) and to a new or modified IEC standard, related to this problem. |  |  | Yes |  |
|  | • If necessary, for reason of quality, the Contractor has the right to change the specified oil type to another similar type, that complies with possible revisions of IEC standards and CIGRE recommendations. |  |  | Yes |  |
|  | 13. Weights and dimensions |  |  |  |  |
|  | • Weights |  |  |  |  |
|  | - Total, ready for operation |  | t | Specify |  |
|  | - Oil |  | t | Specify |  |
|  | - Active part (magnetic circuit + windings) |  | t | Specify |  |
|  | - Core |  | t | Specify |  |
|  | - Windings |  | t | Specify |  |
|  | - Tank |  | t | Specify |  |
|  | • Weight tolerances |  | % | ± 10 |  |
|  | • Transport |  |  |  |  |
|  | - Without oil |  | t | Specify |  |
|  | • Dimensions (ready for operation) |  |  |  |  |
|  | - Length |  | m | Specify |  |
|  | - Width |  | m | Specify |  |
|  | - Height |  | m | Specify |  |
|  | - Height necessary for devatting |  | m | Specify |  |
|  | 14. Painting and corrosion protection |  |  |  |  |
|  | • Procedure for surface treatment |  |  | Specify |  |
|  | • The transformer and its accessories are guaranteed corrosion-free for 10 years. The environment is corrosive, industrial and salty. The supplier guarantees that the paint procedure complies with this requirement |  |  | Yes |  |
|  | • Finishing colour (RAL-code) |  |  | will be specified later |  |
|  | • Tank and large metallic surfaces painting |  |  | Specify |  |
|  | - Internal |  |  |  |  |
|  | . 1 layer anti-rust resistant to oil |  | μm | Specify |  |
|  | - External |  |  |  |  |
|  | . 2 layers anti-rust |  | μm | Specify |  |
|  | . 1 intermediate coat |  | μm | Specify |  |
|  | . 2 finish coats |  | μm | Specify |  |
|  | - Total thickness of the surface treatment |  | μm | Specify |  |
|  | 15. Auxiliary services, accessories, protection |  |  |  |  |
|  | • 1 temperature indicator for winding hot spot equipped with 3 sets of contacts for starting the cooling device |  |  | Yes |  |
|  | • 1 thermometer for top oil temperature equipped 2 sets of contacts (alarms) |  |  | Yes |  |
|  | • 1 empty bag, located on the top of the tank intended for the subsequent mounting of an additional thermometer or thermostat |  |  | Yes |  |
|  | • 1 magnetic oil level indicator on each compartment of the conservator with visible indication and signal contacts for up and down levels |  |  | Yes |  |
|  | • 1 magnetic oil level indicator for oil compartment of the OLTC switch with visible indication and equipped with 1 alarm contact low level |  |  |  |  |
|  | • 1 Buchholz relay with 1 NO (for alarm) and 2 NO contacts for tripping (twin float type) with graduated inspection glass, located between the conservator and the tank |  |  | Yes |  |
|  | • Device to protect the compartment of the tap changer |  |  | Yes |  |
|  | - Pressure relief valve |  |  | Yes |  |
|  | - Buchholz relay (running on the oil flow) |  |  | Yes |  |
|  | • Pressure relief valve (Qualitrol type) installed on the transformer tank, fitted with a contact status indication on / off |  |  | Yes |  |
|  | 16. Documents to be submitted |  |  |  |  |
|  | • Submital fase |  |  | 3 ex. |  |
|  | - Dimension drawing (HV-drawing) with the list of equipment |  |  |  |  |
|  | - Layout drawing showing the accessories,wheels, the position of the bushing and isolation distances required by the transformer |  |  |  |  |
|  | - List of references |  |  |  |  |
|  | • Ordering fase |  |  | 3 ex. |  |
|  | - instruction manual |  |  |  |  |
|  | - erection instruction manual |  |  |  |  |
|  | - maintenance instruction manual |  |  |  |  |
|  | - drawings |  |  |  |  |
|  | - detailed dimensional drawing |  |  |  |  |
|  | - drawing of the rating plate |  |  |  |  |
|  | - LV diagrams |  |  |  |  |
|  | - drawing of electrical circuits |  |  |  |  |
|  | - schematic with the relative position of the windings respect to the core |  |  |  |  |
|  | - Detailed description of the tap changer |  |  |  |  |
|  | - Description of the surface treatment |  |  |  |  |
|  | - Description of the Buchholz relay |  |  |  |  |
|  | - Description of the oil level indicator |  |  |  |  |
|  | - Description of the relief valve |  |  |  |  |
|  | - Description of the dial thermometer temperature |  |  |  |  |
|  | - Description of the sealing device oil / air |  |  |  |  |
|  | - Description of protection devices |  |  |  |  |
|  | - Routine, factory, on site testing reports of similar equipment |  |  |  |  |
|  | • Completed Manufactuer final report including |  |  | 3 ex. |  |
|  | - instruction manual |  |  |  |  |
|  | - erection instruction manual |  |  |  |  |
|  | - maintenance instruction manual |  |  |  |  |
|  | - as built drawings and diagrams |  |  |  |  |
|  | - Detailed layout drawing |  |  |  |  |
|  | - drawing of the LV cabinets |  |  |  |  |
|  | - as built LV diagrams |  |  |  |  |
|  | - schematic with the position of the windings respect to the core |  |  |  |  |
|  | - Drawing of the rating plate |  |  |  |  |
|  | - Detailed description of accessories |  |  |  |  |
|  | - Standard routine, factory, on site test reports |  |  |  |  |
|  | 17. Languages |  |  |  |  |
|  | • All documents establish in English |  |  | Yes |  |

| TECHNICAL SCHEDULE – Main Data AutoTransformer 220/110/10 kV 125MVA |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Description |  |  | Units | Imposed Values | Guaranteed Values |
|  | 1. General characteristics |  |  |  |  |
|  | • Manufacturer |  |  | Specify |  |
|  | • Oil immersed three-phase transformer |  |  | Yes |  |
|  | • Type (Core or Shell) |  |  | Core |  |
|  | • Indoor/Outdoor installation |  |  | Outdoor |  |
|  | • Frequency |  | Hz | 50 |  |
|  | • Number of windings per phase |  |  | 3 |  |
|  | 2. Normal service conditions |  |  |  |  |
|  | • Ambient temperature range |  | °C | -35 to +50 |  |
|  | 3. Rated power, temperature rise and overload |  |  |  |  |
|  | • Cooling mode |  |  | ONAN / ONAF1 / ONAF2 |  |
|  | • Rated power |  |  |  |  |
|  | - primary windings (220kV) |  | MVA | 60 / 90 / 125 |  |
|  | - secondary windings (110kV) |  | MVA | 60 / 90 / 125 |  |
|  | - tertiary windings (10kV) |  | MVA | 40/50/63 |  |
|  | 4. Rated voltages levels |  |  |  |  |
|  | Service Voltages (Un) |  |  |  |  |
|  | - Primary windings |  | kV | 220 |  |
|  | - Secondary windings |  | kV | 110 |  |
|  | - Tertiary windings |  | kV | 10 |  |
|  | Rated Voltages (Ur) |  |  |  |  |
|  | - Primary windings |  | kV | 252 |  |
|  | - Secondary windings |  | kV | 126 |  |
|  | - Tertiary windings |  | kV | 12 |  |
|  | 5. Insulation levels according IEC |  |  |  |  |
|  | • Rated short duration power-frequency withstand voltage (AC) 1min-50Hz (Ud) |  |  |  |  |
|  | - Primary windings |  | kV | 460 |  |
|  | - Secondary windings |  | kV | 230 |  |
|  | - Tertiary windings |  | kV | 28 |  |
|  | • Rated lightning impulse withstand voltage (1,2/50µs) (Up) |  |  |  |  |
|  | - Primary windings |  | kVpeak | 1050 |  |
|  | - Secondary windings |  | kVpeak | 550 |  |
|  | - Tertiary windings |  | kVpeak | 75 |  |
|  | 6. Vector group |  |  | YN,yn0,d11 |  |
|  | 7. Voltage and current characteristics |  |  |  |  |
|  | • Voltage ratio |  | kV | 220/110/10 |  |
|  | • Tapping range on HV side |  | % | ± 10 x1,5% |  |
|  | • Number of taps |  |  | 21 |  |
|  | - Tap nr. 1 (highest ratio) |  | kV | 253 |  |
|  | - Tap nr. 11 (principal tap) |  | kV | 220 |  |
|  | - Tap nr. 21 (lowest ratio) |  | kV | 187 |  |
|  | 8. Losses |  |  |  |  |
|  | • No load loss at rated voltage and frequency (P1) |  |  |  |  |
|  | - Value |  | kW | ≤ 45 |  |
|  | •  45luead loss at rated voltage and frequency (P1)0µs) (Up)C) 1min-50Hz (Ud)g and isolation distances required |  |  |  |  |
|  | - Tap nr. 11 (principal tap) (P2) |  |  |  |  |
|  | . load loss |  | kW | ≤ 230 |  |
|  | 9. Short-circuit impedance |  |  |  |  |
|  | • Short circuit impedance at the rated power of 125 MVA for all the taps of the OLTC |  |  | HV-MV |  |
|  | - Primary / Secondary |  | % | 12 |  |
|  | - Primary / Tertiary |  | % | 10 |  |
|  | - Secondary / Tertiary |  | % | Specify |  |
|  | - Tolerances (on measured values) |  | % | according IEC |  |
|  | 10. Sound level |  |  |  |  |
|  | • Sound level guaranteed and measured according to IEC 60076-10 at principal tap, rated induction and frequency (ONAF) |  | dB(A) | 80 |  |
|  | - Tolerances |  | dB(A) | Specify |  |

| TECHNICAL SCHEDULE – Data for Information AutoTransformer 220/110/10 kV 125MVA |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Description |  |  | Units | Imposed Values | Guaranteed Values |
|  | 1. General characteristics |  |  |  |  |
|  | • Place of manufacture |  |  | Specify |  |
|  | • Standards (latest edition) |  |  | IEC 60076 |  |
|  | • Internal insulation paper and oil |  |  | Yes |  |
|  | • Cooling radiators air / oil fixed on the tank |  |  | Yes |  |
|  | • Oil conservator mounted on the tank |  |  | Yes |  |
|  | 2. Normal service conditions(please refer to the site conditions of each substation) |  |  |  |  |
|  | • Ambient temperature range |  | °C |  |  |
|  | • Relative humidity |  | % |  |  |
|  | • Maximum altitude |  | m |  |  |
|  | • Maximum ice coating |  | mm |  |  |
|  | • Maximum pressure of the wind speed |  | Pa |  |  |
|  | • Solar radiation |  | W/m² |  |  |
|  | 3. Rated power, temperature rise and overload |  |  |  |  |
|  | • Particular operating conditions |  |  |  |  |
|  | - rated power must be considered with the following independent or simultaneous parameter changes: |  |  |  |  |
|  | - variations of the operating voltage (max./min.) |  | kV | 245/205 |  |
|  | - variations of the frequency |  | Hz | 50 +/- 0.5 |  |
|  | • Maximum temperature rise at rated power for all taps and cooling modes |  |  |  |  |
|  | - Top oil temperature rise (by thermometer measurement) |  | K | 60 |  |
|  | - B57 (by temperature probes) |  | K | 65 |  |
|  | - Winding "hot spot" temperature rise |  | K | 78 |  |
|  | 4. Voltage and current characteristics |  |  |  |  |
|  | • Primary nominal current |  | A | Specify |  |
|  | • Secondary nominal current |  | A | Specify |  |
|  | • Tertiary nominal current |  | A | Specify |  |
|  | 5. Tap changer (OLTC) |  |  |  |  |
|  | • Manufacturer |  |  | Specify |  |
|  | • Type: Reinhausen (MR) vaccum type (VACUTAP) or equivalent |  |  | Yes |  |
|  | • Location |  |  |  |  |
|  | - Neutral HV bushing |  |  | NO |  |
|  | - on primary winding |  |  | Yes |  |
|  | • Number of positions |  |  | 21 |  |
|  | • The OLTC supports permanently 120 % of the highest rated current of the transformer |  |  | Specify |  |
|  | • Tapping range |  | % | ± 10 x1,5% |  |
|  | • Rated current |  | A | Specify |  |
|  | • maximum voltage between two successive taps corresponding to In |  | kV | Specify |  |
|  | • Number of switch cycles without maintenance |  |  |  |  |
|  | - At the highest rated current of the transformer |  |  | Specify |  |
|  | - At 1.5 x the highest rated current of the transformer |  |  | Specify |  |
|  | • switching time between two successive taps |  | s | Specify |  |
|  | • transition impedance from resistive-type |  |  | Specify |  |
|  | • Motor drive unit |  |  |  |  |
|  | - Type |  |  | Specify |  |
|  | - Rated supply voltage of the motor |  |  | Specify |  |
|  | 6. Losses |  |  |  |  |
|  | • No load loss at rated voltage and frequency (P1) |  |  |  |  |
|  | - Tolerances |  | % | + 15 |  |
|  |  15lerancesss at rated voltage and frequency (P1)ormerding to Int of the transformereter changes:and frequenc |  |  |  |  |
|  | - Tap nr. 1 |  |  |  |  |
|  | . load loss |  | kW | Specify |  |
|  | . Tolerances |  | % | + 15 |  |
|  | - Tap nr. 11 (principal tap) (P2) |  |  |  |  |
|  | . Tolerances |  | % | + 15 |  |
|  | - Tap nr. 21 |  |  |  |  |
|  | . load loss |  | kW | Specify |  |
|  | . Tolerances |  | % | + 15 |  |
|  | - Total losses (P1 + P2) |  |  |  |  |
|  | . load loss |  | kW | Specify |  |
|  | . Tolerances |  | % | + 10 |  |
|  | • Power taken by cooling equipment (P3) |  |  |  |  |
|  | . Value |  | kW | Specify |  |
|  | 7. Magnetic characteristics |  |  |  |  |
|  | • Permanent over-voltage |  | % | Specify |  |
|  | • Short time duration over-voltage - 3 hours |  | % | Specify |  |
|  | • Magnetic steel: quality |  |  | Specify |  |
|  | - Type of core |  |  | Specify |  |
|  | • Rated induction at rated voltage and frequency. |  | T | Specify |  |
|  | • No-load current (Io) at rated voltage and frequency |  | A | Specify |  |
|  | - No-load current: tolerances |  | % | Specify |  |
|  | • Specific losses of magnetic steel |  | kW | Specify |  |
|  | - Tolerances |  | % | Specify |  |
|  | 8. Overload capabilities |  |  |  |  |
|  | • Overload conditions: subsequent at operating at rated power, average ambient temperature of 40 ° C, hot spot windings temperature limited to 115 ° C |  |  |  |  |
|  | - Overload duration at 120% |  | min | Specify |  |
|  | - Overload duration at 200% |  | min | Specify |  |
|  | • Time constant temperature rises |  |  |  |  |
|  | - Top oil temperature rise |  | h | Specify |  |
|  | - Average winding temperature rise |  | min | Specify |  |
|  | 9. Exceptional service conditions |  |  |  |  |
|  | • Short-circuit withstand capability of the windings ( for every position of the OLTC) |  |  | Yes |  |
|  | - Short-circuit power of the network |  | kA | 40 |  |
|  | - Maximum short-circuit duration (max. Voltage applied, acc. IEC 60909) |  | s | 1 |  |
|  | • direct Impedance / the zero sequence impedance is between 1 and 3 |  |  | Yes |  |
|  | • Maximum allowed value of the average temperature of the windings corresponding, starting from a average temperature of 105 ° C (50 ° C + 55 ° C) |  |  | Specify |  |
|  | 10. Current transformers |  |  |  |  |
|  | • For winding temperature (thermal image) |  |  | Yes |  |
|  | - can be short-circuited in the control cubicle |  |  | Yes |  |
|  | • For other purposes |  |  | No |  |
|  | • Distribution of cores |  |  |  |  |
|  | - side 220kV (phase and neutral) |  |  | N.A. |  |
|  | - side 110kV (phase and neutral) |  |  | N.A. |  |
|  | - side 10kV (phase) |  |  | N.A. |  |
|  | 11. Construction characteristics |  |  |  |  |
|  | Windings |  |  |  |  |
|  | • type of winding line side |  |  | Specify |  |
|  | • Relative position of the windings compared to the magnetic core |  |  | Specify |  |
|  | Cooling |  |  |  |  |
|  | • Cooling mode |  |  | ONAN/ONAF 1/ONAF 2 |  |
|  | • Fans characteristics |  |  | Specify |  |
|  | - Number |  |  | Specify |  |
|  | - Rated power according to IEC standards, within the limits of heating guarantees with coolers |  | MVA | Specify |  |
|  | - Manufacturer |  |  | Specify |  |
|  | - Nature, galvanized steel plates, others |  |  | Specify |  |
|  | • Fans characteristics |  |  |  |  |
|  | - Manufacturer |  |  | Specify |  |
|  | - Type |  |  | Specify |  |
|  | - Number |  |  | Specify |  |
|  | - Power consumption |  | kW | Specify |  |
|  | - Speed |  | rpm | Specify |  |
|  | • Oil conservator |  |  | Yes |  |
|  | - Mounted on the tank on a metal frame |  |  | Yes |  |
|  | - Two separate compartments (transformer and switch of the OLTC) |  |  | Yes |  |
|  | - With rubber expansion membrane (transformer part) |  |  | Yes |  |
|  | - Vacuum filter through and dryer regenerable hygroscopic salts |  |  | Yes |  |
|  | - Maximum allowable over-pressure |  | kPa | 2 |  |
|  | - With filling plug |  |  | Yes |  |
|  | • Tank |  |  |  |  |
|  | - Welded or bolted cover |  |  | Specify |  |
|  | - Allowable over-pressure on cover level |  | kPa | 35 |  |
|  | - Allowable over-pressure on the tank |  | kPa | 2 |  |
|  | - Pressure relief valve (Qualitrol type) |  |  | Yes |  |
|  | - Wheels capable of being directed in two perpendicular directions: |  |  |  |  |
|  | - Number |  |  | 4 |  |
|  | - Inner distances between rails |  |  | Specify |  |
|  | . transversal axle |  | mm | / |  |
|  | . longitudinal axle |  | mm |  |  |
|  | - wheel blocking systems included |  |  |  |  |
|  | • Bushings |  |  |  |  |
|  | • Primary H.V. 220kV (phase) |  |  |  |  |
|  | - Number |  |  | 3 |  |
|  | - Manufacturer |  |  | Specify |  |
|  | - Nature of the internal insulation |  |  | Specify |  |
|  | - Oil - paper |  |  |  |  |
|  | - synthetic resin and paper |  |  |  |  |
|  | • Rated voltage (Ur) |  | kV | 245 |  |
|  | • Rated lightning impulse withstand voltage (Up) |  | kV peak | 1050 |  |
|  | • Rated current (minimum = 120% I rated transformer) |  | A | Specify |  |
|  | - Dry arcing distance |  | mm | Specify |  |
|  | - Developed creepage distance |  | mm/kV | 31 |  |
|  | - Space for bushing CT |  |  | N.A. |  |
|  | • H.V. 220kV (neutral) |  |  |  |  |
|  | - Number |  |  | 1 |  |
|  | - Manufacturer |  |  | Specify |  |
|  | - Nature of the internal insulation |  |  | Specify |  |
|  | - Oil - paper |  |  |  |  |
|  | - synthetic resin and paper |  |  |  |  |
|  | • Rated voltage (Ur) |  | kV | 245 |  |
|  | • Rated lightning impulse withstand voltage (Up) |  | kV peak | 1050 |  |
|  | • Rated current (minimum = 120% I rated transformer) |  | A | Specify |  |
|  | - Dry arcing distance |  | mm | Specify |  |
|  | - Developed creepage distance |  | mm/kV | 31 |  |
|  | - Space for bushing CT |  |  | N.A. |  |
|  | • Secondary H.V. 110kV (phase and neutral) |  |  |  |  |
|  | - Number |  |  | 4 |  |
|  | - Manufacturer |  |  | Specify |  |
|  | - Nature of the internal insulation |  |  | Specify |  |
|  | - Oil - paper |  |  |  |  |
|  | - synthetic resin and paper |  |  |  |  |
|  | • Rated voltage (Ur) |  | kV | 123 |  |
|  | • Rated lightning impulse withstand voltage (Up) |  | kV peak | 550 |  |
|  | • Rated current (minimum = 120% I rated transformer) |  | A | Specify |  |
|  | - Dry arcing distance |  | mm | Specify |  |
|  | - Developed creepage distance |  | mm/kV | 31 |  |
|  | - Space for bushing CT |  |  | N.A. |  |
|  | • Tertiary M.V. 10kV (phase) |  |  |  |  |
|  | - Number |  |  | 3 |  |
|  | - Manufacturer |  |  | Specify |  |
|  | - Nature of the internal insulation |  |  | Specify |  |
|  | - Oil - paper |  |  |  |  |
|  | - synthetic resin and paper |  |  |  |  |
|  | • Rated voltage (Ur) |  | kV | 12 |  |
|  | • Rated lightning impulse withstand voltage (Up) |  | kV peak | 75 |  |
|  | • Rated current (minimum = 120% I rated transformer) |  | A | Specify |  |
|  | - Dry arcing distance |  | mm | Specify |  |
|  | - Developed creepage distance |  | mm/kV | 31 |  |
|  | - Space for bushing CT |  |  | N.A. |  |
|  | 12. Oil |  |  |  |  |
|  | • Oil manufacturer |  |  | Specify |  |
|  | • Oil type (Nynas Nitro or equivalent without PCB, unsulfided and with inhibitor) |  |  | Specify |  |
|  | • Oil with inhibitor |  |  | Yes |  |
|  | - Manufacturer |  |  | Specify |  |
|  | - Type |  |  | Specify |  |
|  | • Conform with IEC 60.296 |  |  | Yes |  |
|  | • The specified oil will be of a non corrosive type. Corrosivity will be checked in accordance to the latest CIGRE recommendations (WG A2-32) and to a new or modified IEC standard, related to this problem. |  |  | Yes |  |
|  | • If necessary, for reason of quality, the Contractor has the right to change the specified oil type to another similar type, that complies with possible revisions of IEC standards and CIGRE recommendations. |  |  | Yes |  |
|  | 13. Weights and dimensions |  |  |  |  |
|  | • Weights |  |  |  |  |
|  | - Total, ready for operation |  | t | Specify |  |
|  | - Oil |  | t | Specify |  |
|  | - Active part (magnetic circuit + windings) |  | t | Specify |  |
|  | - Core |  | t | Specify |  |
|  | - Windings |  | t | Specify |  |
|  | - Tank |  | t | Specify |  |
|  | • Weight tolerances |  | % | ± 10 |  |
|  | • Transport |  |  |  |  |
|  | - Without oil |  | t | Specify |  |
|  | • Dimensions (ready for operation) |  |  |  |  |
|  | - Length |  | m | Specify |  |
|  | - Width |  | m | Specify |  |
|  | - Height |  | m | Specify |  |
|  | - Height necessary for devatting |  | m | Specify |  |
|  | 14. Painting and corrosion protection |  |  |  |  |
|  | • Procedure for surface treatment |  |  | Specify |  |
|  | • The transformer and its accessories are guaranteed corrosion-free for 10 years. The environment is corrosive, industrial and salty. The supplier guarantees that the paint procedure complies with this requirement |  |  | Yes |  |
|  | • Finishing colour (RAL-code) |  |  | will be specified later |  |
|  | • Tank and large metallic surfaces painting |  |  | Specify |  |
|  | - Internal |  |  |  |  |
|  | . 1 layer anti-rust resistant to oil |  | μm | Specify |  |
|  | - External |  |  |  |  |
|  | . 2 layers anti-rust |  | μm | Specify |  |
|  | . 1 intermediate coat |  | μm | Specify |  |
|  | . 2 finish coats |  | μm | Specify |  |
|  | - Total thickness of the surface treatment |  | μm | Specify |  |
|  | 15. Auxiliary services, accessories, protection |  |  |  |  |
|  | • 1 temperature indicator for winding hot spot equipped with 3 sets of contacts for starting the cooling device |  |  | Yes |  |
|  | • 1 thermometer for top oil temperature equipped 2 sets of contacts (alarms) |  |  | Yes |  |
|  | • 1 empty bag, located on the top of the tank intended for the subsequent mounting of an additional thermometer or thermostat |  |  | Yes |  |
|  | • 1 magnetic oil level indicator on each compartment of the conservator with visible indication and signal contacts for up and down levels |  |  | Yes |  |
|  | • 1 magnetic oil level indicator for oil compartment of the OLTC switch with visible indication and equipped with 1 alarm contact low level |  |  |  |  |
|  | • 1 Buchholz relay with 1 NO (for alarm) and 2 NO contacts for tripping (twin float type) with graduated inspection glass, located between the conservator and the tank |  |  | Yes |  |
|  | • Device to protect the compartment of the tap changer |  |  | Yes |  |
|  | - Pressure relief valve |  |  | Yes |  |
|  | - Buchholz relay (running on the oil flow) |  |  | Yes |  |
|  | • Pressure relief valve (Qualitrol type) installed on the transformer tank, fitted with a contact status indication on / off |  |  | Yes |  |
|  | 16. Documents to be submitted |  |  |  |  |
|  | • Submital fase |  |  | 3 ex. |  |
|  | - Dimension drawing (HV-drawing) with the list of equipment |  |  |  |  |
|  | - Layout drawing showing the accessories,wheels, the position of the bushing and isolation distances required by the transformer |  |  |  |  |
|  | - List of references |  |  |  |  |
|  | • Ordering fase |  |  | 3 ex. |  |
|  | - instruction manual |  |  |  |  |
|  | - erection instruction manual |  |  |  |  |
|  | - maintenance instruction manual |  |  |  |  |
|  | - drawings |  |  |  |  |
|  | - detailed dimensional drawing |  |  |  |  |
|  | - drawing of the rating plate |  |  |  |  |
|  | - LV diagrams |  |  |  |  |
|  | - drawing of electrical circuits |  |  |  |  |
|  | - schematic with the relative position of the windings respect to the core |  |  |  |  |
|  | - Detailed description of the tap changer |  |  |  |  |
|  | - Description of the surface treatment |  |  |  |  |
|  | - Description of the Buchholz relay |  |  |  |  |
|  | - Description of the oil level indicator |  |  |  |  |
|  | - Description of the relief valve |  |  |  |  |
|  | - Description of the dial thermometer temperature |  |  |  |  |
|  | - Description of the sealing device oil / air |  |  |  |  |
|  | - Description of protection devices |  |  |  |  |
|  | - Routine, factory, on site testing reports of similar equipment |  |  |  |  |
|  | • Completed Manufactuer final report including |  |  | 3 ex. |  |
|  | - instruction manual |  |  |  |  |
|  | - erection instruction manual |  |  |  |  |
|  | - maintenance instruction manual |  |  |  |  |
|  | - as built drawings and diagrams |  |  |  |  |
|  | - Detailed layout drawing |  |  |  |  |
|  | - drawing of the LV cabinets |  |  |  |  |
|  | - as built LV diagrams |  |  |  |  |
|  | - schematic with the position of the windings respect to the core |  |  |  |  |
|  | - Drawing of the rating plate |  |  |  |  |
|  | - Detailed description of accessories |  |  |  |  |
|  | - Standard routine, factory, on site test reports |  |  |  |  |
|  | 17. Languages |  |  |  |  |
|  | • All documents establish in English |  |  | Yes |  |

| TECHNICAL SCHEDULE – Main Data Power Transformer 110/10 kV 25MVA |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Description |  |  | Units | Imposed Values | Guaranteed Values |
|  | 1. General characteristics |  |  |  |  |
|  | • Manufacturer |  |  | Specify |  |
|  | • Oil immersed three-phase transformer |  |  | Yes |  |
|  | • Type (Core or Shell) |  |  | Core |  |
|  | • Indoor/Outdoor installation |  |  | Outdoor |  |
|  | • Frequency |  | Hz | 50 |  |
|  | • Number of windings per phase |  |  | 2 |  |
|  | 2. Normal service conditions |  |  |  |  |
|  | • Ambient temperature range |  | °C | -35 to +50 |  |
|  | 3. Rated power, temperature rise and overload |  |  |  |  |
|  | • Cooling mode |  |  | ONAN / ONAF1 / ONAF2 |  |
|  | • Rated power |  | MVA | 15/20/25 |  |
|  | 4. Rated voltages levels |  |  |  |  |
|  | Service Voltages (Un) |  |  |  |  |
|  | - Primary windings |  | kV | 110 |  |
|  | - Secondary windings |  | kV | 10 |  |
|  | Rated Voltages (Ur) |  |  |  |  |
|  | - Primary windings |  | kV | 126 |  |
|  | - Secondary windings |  | kV | 12 |  |
|  | 5. Insulation levels according IEC |  |  |  |  |
|  | • Rated short duration power-frequency withstand voltage (AC) 1min-50Hz (Ud) |  |  |  |  |
|  | - Primary windings |  | kV | 230 |  |
|  | - Secondary windings |  | kV | 28 |  |
|  | • Rated lightning impulse withstand voltage (1,2/50µs) (Up) |  |  |  |  |
|  | - Primary windings |  | kVpeak | 550 |  |
|  | - Secondary windings |  | kVpeak | 75 |  |
|  | 6. Vector group |  |  | YN,d11 |  |
|  | 7. Voltage and current characteristics |  |  |  |  |
|  | • Voltage ratio |  | kV | 110/10 |  |
|  | • Tapping range on HV side |  | % | ± 10 x1,5% |  |
|  | • Number of taps |  |  | 21 |  |
|  | - Tap nr. 1 (highest ratio) |  | kV | 126,5 |  |
|  | - Tap nr. 11 (principal tap) |  | kV | 110 |  |
|  | - Tap nr. 21 (lowest ratio) |  | kV | 93,5 |  |
|  | 8. Losses |  |  |  |  |
|  | • No load loss at rated voltage and frequency (P1) |  |  |  |  |
|  | - Value |  | kW | ≤ 10 |  |
|  | • Load loss between HV and MV at rated power of 25 MVA and an average temperature of the windings of 75°C (P2) |  |  |  |  |
|  | - Tap nr. 11 (principal tap) (P2) |  |  |  |  |
|  | . load loss |  | kW | ≤ 50 |  |
|  | 9. Short-circuit impedance |  |  |  |  |
|  | • Short circuit impedance at the rated power of 25 MVA for all the taps of the OLTC |  | % | 10 |  |
|  | - Tolerances (on measured values) |  | % | according IEC |  |
|  | 10. Sound level |  |  |  |  |
|  | • Sound level guaranteed and measured according to IEC 60076-10 at principal tap, rated induction and frequency (ONAF) |  | dB(A) | ≤ 72 |  |
|  | • All documents establish in English |  |  | Yes |  |

| TECHNICAL SCHEDULE – Data for Information Power Transformer 110/10 kV 25MVA |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Description |  |  | Units | Imposed Values | Guaranteed Values |
|  | 1. General characteristics |  |  |  |  |
|  | • Place of manufacture |  |  | Specify |  |
|  | • Standards (latest edition) |  |  | IEC 60076 |  |
|  | • Internal insulation paper and oil |  |  | Yes |  |
|  | • Cooling radiators air / oil fixed on the tank |  |  | Yes |  |
|  | • Oil conservator mounted on the tank |  |  | Yes |  |
|  | 2. Normal service conditions(please refer to the site conditions of each substation) |  |  |  |  |
|  | • Ambient temperature range |  | °C |  |  |
|  | • Relative humidity |  | % |  |  |
|  | • Maximum altitude |  | m |  |  |
|  | • Maximum ice coating |  | mm |  |  |
|  | • Maximum pressure of the wind speed |  | Pa |  |  |
|  | • Solar radiation |  | W/m² |  |  |
|  | 3. Rated power, temperature rise and overload |  |  |  |  |
|  | • Particular operating conditions |  |  |  |  |
|  | - rated power must be considered with the following independent or simultaneous parameter changes: |  |  |  |  |
|  | - variations of the operating voltage (max./min.) |  | kV | 120/100 |  |
|  | - variations of the frequency |  | Hz | 50 +/- 0.5 |  |
|  | • Maximum temperature rise at rated power for all taps and cooling modes |  |  |  |  |
|  | - Top oil temperature rise (by thermometer measurement) |  | K | 60 |  |
|  | - B57 (by temperature probes) |  | K | 65 |  |
|  | - Winding "hot spot" temperature rise |  | K | 78 |  |
|  | 4. Voltage and current characteristics |  |  |  |  |
|  | • Primary nominal current |  | A | Specify |  |
|  | • Secondary nominal current |  | A | Specify |  |
|  | 5. Tap changer (OLTC) |  |  |  |  |
|  | • Manufacturer |  |  | Specify |  |
|  | • Type: Reinhausen (MR) vaccum type (VACUTAP) or equivalent |  |  | Yes |  |
|  | • Location |  |  |  |  |
|  | - Neutral HV bushing |  |  | NO |  |
|  | - on primary winding |  |  | Yes |  |
|  | • Number of positions |  |  | 21 |  |
|  | • The OLTC supports permanently 120 % of the highest rated current of the transformer |  |  | Specify |  |
|  | • Tapping range |  | % | ± 10 x1,5% |  |
|  | • Rated current |  | A | Specify |  |
|  | • maximum voltage between two successive taps corresponding to In |  | kV | Specify |  |
|  | • Number of switch cycles without maintenance |  |  |  |  |
|  | - At the highest rated current of the transformer |  |  | Specify |  |
|  | - At 1.5 x the highest rated current of the transformer |  |  | Specify |  |
|  | • switching time between two successive taps |  | s | Specify |  |
|  | • transition impedance from resistive-type |  |  | Specify |  |
|  | • Motor drive unit |  |  |  |  |
|  | - Type |  |  | Specify |  |
|  | - Rated supply voltage of the motor |  |  | Specify |  |
|  | 6. Losses |  |  |  |  |
|  | • No load loss at rated voltage and frequency (P1) |  |  |  |  |
|  | - Tolerances |  | % | + 15 |  |
|  | • Load loss between HV and MV at rated power of 25 MVA and an average temperature of the windings of 75°C (P2) |  |  |  |  |
|  | - Tap nr. 1 |  |  |  |  |
|  | . load loss |  | kW | Specify |  |
|  | . Tolerances |  | % | + 15 |  |
|  | - Tap nr. 11 (principal tap) (P2) |  |  |  |  |
|  | . Tolerances |  | % | + 15 |  |
|  | - Tap nr. 21 |  |  |  |  |
|  | . load loss |  | kW | Specify |  |
|  | . Tolerances |  | % | + 15 |  |
|  | - Total losses (P1 + P2) |  |  |  |  |
|  | . load loss |  | kW | Specify |  |
|  | . Tolerances |  | % | + 10 |  |
|  | • Power taken by cooling equipment (P3) |  |  |  |  |
|  | . Value |  | kW | Specify |  |
|  | 7. Magnetic characteristics |  |  |  |  |
|  | • Permanent over-voltage |  | % | Specify |  |
|  | • Short time duration over-voltage - 3 hours |  | % | Specify |  |
|  | • Magnetic steel: quality |  |  | Specify |  |
|  | - Type of core |  |  | Specify |  |
|  | • Rated induction at rated voltage and frequency. |  | T | Specify |  |
|  | • No-load current (Io) at rated voltage and frequency |  | A | Specify |  |
|  | - No-load current: tolerances |  | % | Specify |  |
|  | • Specific losses of magnetic steel |  | kW | Specify |  |
|  | - Tolerances |  | % | Specify |  |
|  | 8. Overload capabilities |  |  |  |  |
|  | • Overload conditions: subsequent at operating at rated power, average ambient temperature of 40 ° C, hot spot windings temperature limited to 115 ° C |  |  |  |  |
|  | - Overload duration at 120% |  | min | Specify |  |
|  | - Overload duration at 200% |  | min | Specify |  |
|  | • Time constant temperature rises |  |  |  |  |
|  | - Top oil temperature rise |  | h | Specify |  |
|  | - Average winding temperature rise |  | min | Specify |  |
|  | 9. Exceptional service conditions |  |  |  |  |
|  | • Short-circuit withstand capability of the windings ( for every position of the OLTC) |  |  | Yes |  |
|  | - Short-circuit power of the network |  | kA | 31.5 |  |
|  | - Maximum short-circuit duration (max. Voltage applied, acc. IEC 60909) |  | s | 1 |  |
|  | • direct Impedance / the zero sequence impedance is between 1 and 3 |  |  | Yes |  |
|  | • Maximum allowed value of the average temperature of the windings corresponding, starting from a average temperature of 105 ° C (50 ° C + 55 ° C) |  |  | Specify |  |
|  | 10. Current transformers |  |  |  |  |
|  | • For winding temperature (thermal image) |  |  | Yes |  |
|  | - can be short-circuited in the control cubicle |  |  | Yes |  |
|  | • For other purposes |  |  | No |  |
|  | • Distribution of cores |  |  |  |  |
|  | - side 110kV (phase and neutral) |  |  | N.A. |  |
|  | - side 10kV (phase) |  |  | N.A. |  |
|  | 11. Construction characteristics |  |  |  |  |
|  | Windings |  |  |  |  |
|  | • type of winding line side |  |  | Specify |  |
|  | • Relative position of the windings compared to the magnetic core |  |  | Specify |  |
|  | Cooling |  |  |  |  |
|  | • Cooling mode |  |  | ONAN/ONAF 1/ ONAF 2 |  |
|  | • Fans characteristics |  |  | Specify |  |
|  | - Number |  |  | Specify |  |
|  | - Rated power according to IEC standards, within the limits of heating guarantees with coolers |  | MVA | Specify |  |
|  | - Manufacturer |  |  | Specify |  |
|  | - Nature, galvanized steel plates, others |  |  | Specify |  |
|  | • Fans characteristics |  |  |  |  |
|  | - Manufacturer |  |  | Specify |  |
|  | - Type |  |  | Specify |  |
|  | - Number |  |  | Specify |  |
|  | - Power consumption |  | kW | Specify |  |
|  | - Speed |  | rpm | Specify |  |
|  | • Oil conservator |  |  | Yes |  |
|  | - Mounted on the tank on a metal frame |  |  | Yes |  |
|  | - Two separate compartments (transformer and switch of the OLTC) |  |  | Yes |  |
|  | - With rubber expansion membrane (transformer part) |  |  | Yes |  |
|  | - Vacuum filter through and dryer regenerable hygroscopic salts |  |  | Yes |  |
|  | - Maximum allowable over-pressure |  | kPa | 2 |  |
|  | - With filling plug |  |  | Yes |  |
|  | • Tank |  |  |  |  |
|  | - Welded or bolted cover |  |  | Specify |  |
|  | - Allowable over-pressure on cover level |  | kPa | 35 |  |
|  | - Allowable over-pressure on the tank |  | kPa | 2 |  |
|  | - Pressure relief valve (Qualitrol type) |  |  | Yes |  |
|  | - Wheels capable of being directed in two perpendicular directions: |  |  |  |  |
|  | - Number |  |  | 4 |  |
|  | - Inner distances between rails |  |  | Specify |  |
|  | . transversal axle |  | mm | / |  |
|  | . longitudinal axle |  | mm |  |  |
|  | - wheel blocking systems included |  |  |  |  |
|  | • Bushings |  |  |  |  |
|  | • Primary H.V. 110kV (phase and neutral) |  |  |  |  |
|  | - Number |  |  | 4 |  |
|  | - Manufacturer |  |  | Specify |  |
|  | - Nature of the internal insulation |  |  | Specify |  |
|  | - Oil - paper |  |  |  |  |
|  | - synthetic resin and paper |  |  |  |  |
|  | • Rated voltage (Ur) |  | kV | 123 |  |
|  | • Rated lightning impulse withstand voltage (Up) |  | kV peak | 550 |  |
|  | • Rated current (minimum = 120% I rated transformer) |  | A | Specify |  |
|  | - Dry arcing distance |  | mm | Specify |  |
|  | - Developed creepage distance |  | mm/kV | 31 |  |
|  | - Space for bushing CT |  |  | N.A. |  |
|  | • Secondary M.V. 10kV |  |  |  |  |
|  | - Number |  |  | 3 |  |
|  | - Manufacturer |  |  | Specify |  |
|  | - Nature of the internal insulation |  |  | Specify |  |
|  | - Oil - paper |  |  |  |  |
|  | - synthetic resin and paper |  |  |  |  |
|  | • Rated voltage (Ur) |  | kV | 12 |  |
|  | • Rated lightning impulse withstand voltage (Up) |  | kV peak | 75 |  |
|  | • Rated current (minimum = 120% I rated transformer) |  | A | Specify |  |
|  | - Dry arcing distance |  | mm | Specify |  |
|  | - Developed creepage distance |  | mm/kV | 31 |  |
|  | - Space for bushing CT |  |  | N.A. |  |
|  | 12. Oil |  |  |  |  |
|  | • Oil manufacturer |  |  | Specify |  |
|  | • Oil type (Nynas Nitro or equivalent without PCB, unsulfided and with inhibitor) |  |  | Specify |  |
|  | • Oil with inhibitor |  |  | Yes |  |
|  | - Manufacturer |  |  | Specify |  |
|  | - Type |  |  | Specify |  |
|  | • Conform with IEC 60.296 |  |  | Yes |  |
|  | • The specified oil will be of a non corrosive type. Corrosivity will be checked in accordance to the latest CIGRE recommendations (WG A2-32) and to a new or modified IEC standard, related to this problem. |  |  | Yes |  |
|  | • If necessary, for reason of quality, the Contractor has the right to change the specified oil type to another similar type, that complies with possible revisions of IEC standards and CIGRE recommendations. |  |  | Yes |  |
|  | 13. Weights and dimensions |  |  |  |  |
|  | • Weights |  |  |  |  |
|  | - Total, ready for operation |  | t | Specify |  |
|  | - Oil |  | t | Specify |  |
|  | - Active part (magnetic circuit + windings) |  | t | Specify |  |
|  | - Core |  | t | Specify |  |
|  | - Windings |  | t | Specify |  |
|  | - Tank |  | t | Specify |  |
|  | • Weight tolerances |  | % | ± 10 |  |
|  | • Transport |  |  |  |  |
|  | - Without oil |  | t | Specify |  |
|  | • Dimensions (ready for operation) |  |  |  |  |
|  | - Length |  | m | Specify |  |
|  | - Width |  | m | Specify |  |
|  | - Height |  | m | Specify |  |
|  | - Height necessary for devatting |  | m | Specify |  |
|  | 14. Painting and corrosion protection |  |  |  |  |
|  | • Procedure for surface treatment |  |  | Specify |  |
|  | • The transformer and its accessories are guaranteed corrosion-free for 10 years. The environment is corrosive, industrial and salty. The supplier guarantees that the paint procedure complies with this requirement |  |  | Yes |  |
|  | • Finishing colour (RAL-code) |  |  | will be specified later |  |
|  | • Tank and large metallic surfaces painting |  |  | Specify |  |
|  | - Internal |  |  |  |  |
|  | . 1 layer anti-rust resistant to oil |  | μm | Specify |  |
|  | - External |  |  |  |  |
|  | . 2 layers anti-rust |  | μm | Specify |  |
|  | . 1 intermediate coat |  | μm | Specify |  |
|  | . 2 finish coats |  | μm | Specify |  |
|  | - Total thickness of the surface treatment |  | μm | Specify |  |
|  | 15. Auxiliary services, accessories, protection |  |  |  |  |
|  | • 1 temperature indicator for winding hot spot equipped with 3 sets of contacts for starting the cooling device |  |  | Yes |  |
|  | • 1 thermometer for top oil temperature equipped 2 sets of contacts (alarms) |  |  | Yes |  |
|  | • 1 empty bag, located on the top of the tank intended for the subsequent mounting of an additional thermometer or thermostat |  |  | Yes |  |
|  | • 1 magnetic oil level indicator on each compartment of the conservator with visible indication and signal contacts for up and down levels |  |  | Yes |  |
|  | • 1 magnetic oil level indicator for oil compartment of the OLTC switch with visible indication and equipped with 1 alarm contact low level |  |  |  |  |
|  | • 1 Buchholz relay with 1 NO (for alarm) and 2 NO contacts for tripping (twin float type) with graduated inspection glass, located between the conservator and the tank |  |  | Yes |  |
|  | • Device to protect the compartment of the tap changer |  |  | Yes |  |
|  | - Pressure relief valve |  |  | Yes |  |
|  | - Buchholz relay (running on the oil flow) |  |  | Yes |  |
|  | • Pressure relief valve (Qualitrol type) installed on the transformer tank, fitted with a contact status indication on / off |  |  | Yes |  |
|  | 16. Documents to be submitted |  |  |  |  |
|  | • Submital fase |  |  | 3 ex. |  |
|  | - Dimension drawing (HV-drawing) with the list of equipment |  |  |  |  |
|  | - Layout drawing showing the accessories,wheels, the position of the bushing and isolation distances required by the transformer |  |  |  |  |
|  | - List of references |  |  |  |  |
|  | • Ordering fase |  |  | 3 ex. |  |
|  | - instruction manual |  |  |  |  |
|  | - erection instruction manual |  |  |  |  |
|  | - maintenance instruction manual |  |  |  |  |
|  | - drawings |  |  |  |  |
|  | - detailed dimensional drawing |  |  |  |  |
|  | - drawing of the rating plate |  |  |  |  |
|  | - LV diagrams |  |  |  |  |
|  | - drawing of electrical circuits |  |  |  |  |
|  | - schematic with the relative position of the windings respect to the core |  |  |  |  |
|  | - Detailed description of the tap changer |  |  |  |  |
|  | - Description of the surface treatment |  |  |  |  |
|  | - Description of the Buchholz relay |  |  |  |  |
|  | - Description of the oil level indicator |  |  |  |  |
|  | - Description of the relief valve |  |  |  |  |
|  | - Description of the dial thermometer temperature |  |  |  |  |
|  | - Description of the sealing device oil / air |  |  |  |  |
|  | - Description of protection devices |  |  |  |  |
|  | - Routine, factory, on site testing reports of similar equipment |  |  |  |  |
|  | • Completed Manufactuer final report including |  |  | 3 ex. |  |
|  | - instruction manual |  |  |  |  |
|  | - erection instruction manual |  |  |  |  |
|  | - maintenance instruction manual |  |  |  |  |
|  | - as built drawings and diagrams |  |  |  |  |
|  | - Detailed layout drawing |  |  |  |  |
|  | - drawing of the LV cabinets |  |  |  |  |
|  | - as built LV diagrams |  |  |  |  |
|  | - schematic with the position of the windings respect to the core |  |  |  |  |
|  | - Drawing of the rating plate |  |  |  |  |
|  | - Detailed description of accessories |  |  |  |  |
|  | - Standard routine, factory, on site test reports |  |  |  |  |
|  | 17. Languages |  |  |  |  |
|  | • All documents establish in English |  |  | Yes |  |

| TECHNICAL SCHEDULE – Main Data Boost Transformer 10/10 kV 40MVA |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Description |  |  | Units | Imposed Values | Guaranteed Values |
|  | 1. General characteristics |  |  |  |  |
|  | • Manufacturer |  |  | Specify |  |
|  | • Oil immersed three-phase transformer |  |  | Yes |  |
|  | • Type (Core or Shell) |  |  | Core |  |
|  | • Indoor/Outdoor installation |  |  | Outdoor |  |
|  | • Frequency |  | Hz | 50 |  |
|  | • Number of windings per phase |  |  | 2 |  |
|  | 2. Normal service conditions |  |  |  |  |
|  | • Ambient temperature range |  | °C | -35 to +50 |  |
|  | 3. Rated power, temperature rise and overload |  |  |  |  |
|  | • Cooling mode |  |  | ONAN / ONAF1 / ONAF2 |  |
|  | • Rated power |  | MVA | 20/30/40 |  |
|  | 4. Rated voltages levels |  |  |  |  |
|  | Service Voltages (Un) |  |  |  |  |
|  | - Primary windings |  | kV | 10 |  |
|  | - Secondary windings |  | kV | 10 |  |
|  | Rated Voltages (Ur) |  |  |  |  |
|  | - Primary windings |  | kV | 12 |  |
|  | - Secondary windings |  | kV | 12 |  |
|  | 5. Insulation levels according IEC |  |  |  |  |
|  | • Rated short duration power-frequency withstand voltage (AC) 1min-50Hz (Ud) |  |  |  |  |
|  | - Primary windings |  | kV | 28 |  |
|  | - Secondary windings |  | kV | 28 |  |
|  | • Rated lightning impulse withstand voltage (1,2/50µs) (Up) |  |  |  |  |
|  | - Primary windings |  | kVpeak | 75 |  |
|  | - Secondary windings |  | kVpeak | 75 |  |
|  | 6. Vector group |  |  | D,d4 |  |
|  | 7. Voltage and current characteristics |  |  |  |  |
|  | • Voltage ratio |  | kV | 10/10 |  |
|  | • Tapping range on HV side |  | % | ± 10 x1,5% |  |
|  | • Number of taps |  |  | 21 |  |
|  | - Tap nr. 1 (highest ratio) |  | kV | 11,5 |  |
|  | - Tap nr. 11 (principal tap) |  | kV | 10 |  |
|  | - Tap nr. 21 (lowest ratio) |  | kV | 8,5 |  |
|  | 9. Losses |  |  |  |  |
|  | • No load loss at rated voltage and frequency (P1) |  |  |  |  |
|  | - Value |  | kW | ≤ 20 |  |
|  | • Load loss between HV and MV at rated power of 20 MVA and an average temperature of the windings of 75°C (P2) |  |  |  |  |
|  | - Tap nr. 11 (principal tap) (P2) |  |  |  |  |
|  | . load loss |  | kW | ≤ 80 |  |
|  | 10. Short-circuit impedance |  |  |  |  |
|  | • Short circuit impedance at the rated power of 40 MVA for all the taps of the OLTC |  | % | 10 |  |
|  | - Tolerances (on measured values) |  | % | according IEC |  |
|  | 14. Sound level |  |  |  |  |
|  | • Sound level guaranteed and measured according to IEC 60076-10 at principal tap, rated induction and frequency (ONAF) |  | dB(A) | ≤ 72 |  |
|  | - Tolerances |  | dB(A) | Specify |  |

| TECHNICAL SCHEDULE – Data for Information Boost Transformer 10/10 kV 40MVA |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Description |  |  | Units | Imposed Values | Guaranteed Values |
|  | 1. General characteristics |  |  |  |  |
|  | • Place of manufacture |  |  | Specify |  |
|  | • Standards (latest edition) |  |  | IEC 60076 |  |
|  | • Internal insulation paper and oil |  |  | Yes |  |
|  | • Cooling radiators air / oil fixed on the tank |  |  | Yes |  |
|  | • Oil conservator mounted on the tank |  |  | Yes |  |
|  | 2. Normal service conditions(please refer to the site conditions of each substation) |  |  |  |  |
|  | • Ambient temperature range |  | °C |  |  |
|  | • Relative humidity |  | % |  |  |
|  | • Maximum altitude |  | m |  |  |
|  | • Maximum ice coating |  | mm |  |  |
|  | • Maximum pressure of the wind speed |  | Pa |  |  |
|  | • Solar radiation |  | W/m² |  |  |
|  | 3. Rated power, temperature rise and overload |  |  |  |  |
|  | • Particular operating conditions |  |  |  |  |
|  | - rated power must be considered with the following independent or simultaneous parameter changes: |  |  |  |  |
|  | - variations of the operating voltage (max./min.) |  | kV | 9,5/10,5 |  |
|  | - variations of the frequency |  | Hz | 50 +/- 0.5 |  |
|  | • Maximum temperature rise at rated power for all taps and cooling modes |  |  |  |  |
|  | - Top oil temperature rise (by thermometer measurement) |  | K | 60 |  |
|  | - B57 (by temperature probes) |  | K | 65 |  |
|  | - Winding "hot spot" temperature rise |  | K | 78 |  |
|  | 4. Voltage and current characteristics |  |  |  |  |
|  | • Primary nominal current |  | A | Specify |  |
|  | • Secondary nominal current |  | A | Specify |  |
|  | 5. Tap changer (OLTC) |  |  |  |  |
|  | • Manufacturer |  |  | Specify |  |
|  | • Type: Reinhausen (MR) vaccum type (VACUTAP) or equivalent |  |  | Yes |  |
|  | • Location |  |  |  |  |
|  | - Neutral HV bushing |  |  | NO |  |
|  | - on primary winding |  |  | Yes |  |
|  | • Number of positions |  |  | 21 |  |
|  | • The OLTC supports permanently 120 % of the highest rated current of the transformer |  |  | Specify |  |
|  | • Tapping range |  | % | ± 10 x1,5% |  |
|  | • Rated current |  | A | Specify |  |
|  | • maximum voltage between two successive taps corresponding to In |  | kV | Specify |  |
|  | • Number of switch cycles without maintenance |  |  |  |  |
|  | - At the highest rated current of the transformer |  |  | Specify |  |
|  | - At 1.5 x the highest rated current of the transformer |  |  | Specify |  |
|  | • switching time between two successive taps |  | s | Specify |  |
|  | • transition impedance from resistive-type |  |  | Specify |  |
|  | • Motor drive unit |  |  |  |  |
|  | - Type |  |  | Specify |  |
|  | - Rated supply voltage of the motor |  |  | Specify |  |
|  | 6. Losses |  |  |  |  |
|  | • No load loss at rated voltage and frequency (P1) |  |  |  |  |
|  | - Tolerances |  | % | + 15 |  |
|  |  15lerancesss at rated voltage and frequency (P1)ormerding to Int of the transformereter changes:and  |  |  |  |  |
|  | - Tap nr. 1 |  |  |  |  |
|  | . load loss |  | kW | Specify |  |
|  | . Tolerances |  | % | + 15 |  |
|  | - Tap nr. 11 (principal tap) (P2) |  |  |  |  |
|  | . Tolerances |  | % | + 15 |  |
|  | - Tap nr. 21 |  |  |  |  |
|  | . load loss |  | kW | Specify |  |
|  | . Tolerances |  | % | + 15 |  |
|  | - Total losses (P1 + P2) |  |  |  |  |
|  | . load loss |  | kW | Specify |  |
|  | . Tolerances |  | % | + 10 |  |
|  | • Power taken by cooling equipment (P3) |  |  |  |  |
|  | . Value |  | kW | Specify |  |
|  | 7. Magnetic characteristics |  |  |  |  |
|  | • Permanent over-voltage |  | % | Specify |  |
|  | • Short time duration over-voltage - 3 hours |  | % | Specify |  |
|  | • Magnetic steel: quality |  |  | Specify |  |
|  | - Type of core |  |  | Specify |  |
|  | • Rated induction at rated voltage and frequency. |  | T | Specify |  |
|  | • No-load current (Io) at rated voltage and frequency |  | A | Specify |  |
|  | - No-load current: tolerances |  | % | Specify |  |
|  | • Specific losses of magnetic steel |  | kW | Specify |  |
|  | - Tolerances |  | % | Specify |  |
|  | 8. Overload capabilities |  |  |  |  |
|  | • Overload conditions: subsequent at operating at rated power, average ambient temperature of 40 ° C, hot spot windings temperature limited to 115 ° C |  |  |  |  |
|  | - Overload duration at 120% |  | min | Specify |  |
|  | - Overload duration at 200% |  | min | Specify |  |
|  | • Time constant temperature rises |  |  |  |  |
|  | - Top oil temperature rise |  | h | Specify |  |
|  | - Average winding temperature rise |  | min | Specify |  |
|  | 9. Exceptional service conditions |  |  |  |  |
|  | • Short-circuit withstand capability of the windings ( for every position of the OLTC) |  |  | Yes |  |
|  | - Short-circuit power of the network |  | kA | 40 |  |
|  | - Maximum short-circuit duration (max. Voltage applied, acc. IEC 60909) |  | s | 1 |  |
|  | • direct Impedance / the zero sequence impedance is between 1 and 3 |  |  | Yes |  |
|  | • Maximum allowed value of the average temperature of the windings corresponding, starting from a average temperature of 105 ° C (50 ° C + 55 ° C) |  |  | Specify |  |
|  | 10. Current transformers |  |  |  |  |
|  | • For winding temperature (thermal image) |  |  | Yes |  |
|  | - can be short-circuited in the control cubicle |  |  | Yes |  |
|  | • For other purposes |  |  | No |  |
|  | 11. Construction characteristics |  |  |  |  |
|  | Windings |  |  |  |  |
|  | • type of winding line side |  |  | Specify |  |
|  | • Relative position of the windings compared to the magnetic core |  |  | Specify |  |
|  | Cooling |  |  |  |  |
|  | • Cooling mode |  |  | ONAN/ONAF |  |
|  | • Fans characteristics |  |  | Specify |  |
|  | - Number |  |  | Specify |  |
|  | - Rated power according to IEC standards, within the limits of heating guarantees with coolers |  | MVA | Specify |  |
|  | - Manufacturer |  |  | Specify |  |
|  | - Nature, galvanized steel plates, others |  |  | Specify |  |
|  | • Fans characteristics |  |  |  |  |
|  | - Manufacturer |  |  | Specify |  |
|  | - Type |  |  | Specify |  |
|  | - Number |  |  | Specify |  |
|  | - Power consumption |  | kW | Specify |  |
|  | - Speed |  | rpm | Specify |  |
|  | • Oil conservator |  |  | Yes |  |
|  | - Mounted on the tank on a metal frame |  |  | Yes |  |
|  | - Two separate compartments (transformer and switch of the OLTC) |  |  | Yes |  |
|  | - With rubber expansion membrane (transformer part) |  |  | Yes |  |
|  | - Vacuum filter through and dryer regenerable hygroscopic salts |  |  | Yes |  |
|  | - Maximum allowable over-pressure |  | kPa | 2 |  |
|  | - With filling plug |  |  | Yes |  |
|  | • Tank |  |  |  |  |
|  | - Welded or bolted cover |  |  | Specify |  |
|  | - Allowable over-pressure on cover level |  | kPa | 35 |  |
|  | - Allowable over-pressure on the tank |  | kPa | 2 |  |
|  | - Pressure relief valve (Qualitrol type) |  |  | Yes |  |
|  | - Wheels capable of being directed in two perpendicular directions: |  |  |  |  |
|  | - Number |  |  | 4 |  |
|  | - Inner distances between rails |  |  | Specify |  |
|  | . transversal axle |  | mm | / |  |
|  | . longitudinal axle |  | mm |  |  |
|  | - wheel blocking systems included |  |  |  |  |
|  | • Bushings |  |  |  |  |
|  | • Primary M.V. 10kV (phase and neutral) |  |  |  |  |
|  | - Number |  |  | 4 |  |
|  | - Manufacturer |  |  | Specify |  |
|  | - Nature of the internal insulation |  |  | Specify |  |
|  | - Oil - paper |  |  |  |  |
|  | - synthetic resin and paper |  |  |  |  |
|  | • Rated voltage (Ur) |  | kV | 12 |  |
|  | • Rated lightning impulse withstand voltage (Up) |  | kV peak | 75 |  |
|  | • Rated current (minimum = 120% I rated transformer) |  | A | Specify |  |
|  | - Dry arcing distance |  | mm | Specify |  |
|  | - Developed creepage distance |  | mm/kV | 31 |  |
|  | - Space for bushing CT |  |  | N.A. |  |
|  | • Secondary M.V. 10kV |  |  |  |  |
|  | - Number |  |  | 3 |  |
|  | - Manufacturer |  |  | Specify |  |
|  | - Nature of the internal insulation |  |  | Specify |  |
|  | - Oil - paper |  |  |  |  |
|  | - synthetic resin and paper |  |  |  |  |
|  | • Rated voltage (Ur) |  | kV | 12 |  |
|  | • Rated lightning impulse withstand voltage (Up) |  | kV peak | 75 |  |
|  | • Rated current (minimum = 120% I rated transformer) |  | A | Specify |  |
|  | - Dry arcing distance |  | mm | Specify |  |
|  | - Developed creepage distance |  | mm/kV | 31 |  |
|  | - Space for bushing CT |  |  | N.A. |  |
|  | 12. Oil |  |  |  |  |
|  | • Oil manufacturer |  |  | Specify |  |
|  | • Oil type (Nynas Nitro or equivalent without PCB, unsulfided and with inhibitor) |  |  | Specify |  |
|  | • Oil with inhibitor |  |  | Yes |  |
|  | - Manufacturer |  |  | Specify |  |
|  | - Type |  |  | Specify |  |
|  | • Conform with IEC 60.296 |  |  | Yes |  |
|  | • The specified oil will be of a non corrosive type. Corrosivity will be checked in accordance to the latest CIGRE recommendations (WG A2-32) and to a new or modified IEC standard, related to this problem. |  |  | Yes |  |
|  | • If necessary, for reason of quality, the Contractor has the right to change the specified oil type to another similar type, that complies with possible revisions of IEC standards and CIGRE recommendations. |  |  | Yes |  |
|  | 13. Weights and dimensions |  |  |  |  |
|  | • Weights |  |  |  |  |
|  | - Total, ready for operation |  | t | Specify |  |
|  | - Oil |  | t | Specify |  |
|  | - Active part (magnetic circuit + windings) |  | t | Specify |  |
|  | - Core |  | t | Specify |  |
|  | - Windings |  | t | Specify |  |
|  | - Tank |  | t | Specify |  |
|  | • Weight tolerances |  | % | ± 10 |  |
|  | • Transport |  |  |  |  |
|  | - Without oil |  | t | Specify |  |
|  | • Dimensions (ready for operation) |  |  |  |  |
|  | - Length |  | m | Specify |  |
|  | - Width |  | m | Specify |  |
|  | - Height |  | m | Specify |  |
|  | - Height necessary for devatting |  | m | Specify |  |
|  | 14. Painting and corrosion protection |  |  |  |  |
|  | • Procedure for surface treatment |  |  | Specify |  |
|  | • The transformer and its accessories are guaranteed corrosion-free for 10 years. The environment is corrosive, industrial and salty. The supplier guarantees that the paint procedure complies with this requirement |  |  | Yes |  |
|  | • Finishing colour (RAL-code) |  |  | will be specified later |  |
|  | • Tank and large metallic surfaces painting |  |  | Specify |  |
|  | - Internal |  |  |  |  |
|  | . 1 layer anti-rust resistant to oil |  | μm | Specify |  |
|  | - External |  |  |  |  |
|  | . 2 layers anti-rust |  | μm | Specify |  |
|  | . 1 intermediate coat |  | μm | Specify |  |
|  | . 2 finish coats |  | μm | Specify |  |
|  | - Total thickness of the surface treatment |  | μm | Specify |  |
|  | 15. Auxiliary services, accessories, protection |  |  |  |  |
|  | • 1 temperature indicator for winding hot spot equipped with 3 sets of contacts for starting the cooling device |  |  | Yes |  |
|  | • 1 thermometer for top oil temperature equipped 2 sets of contacts (alarms) |  |  | Yes |  |
|  | • 1 empty bag, located on the top of the tank intended for the subsequent mounting of an additional thermometer or thermostat |  |  | Yes |  |
|  | • 1 magnetic oil level indicator on each compartment of the conservator with visible indication and signal contacts for up and down levels |  |  | Yes |  |
|  | • 1 magnetic oil level indicator for oil compartment of the OLTC switch with visible indication and equipped with 1 alarm contact low level |  |  |  |  |
|  | • 1 Buchholz relay with 1 NO (for alarm) and 2 NO contacts for tripping (twin float type) with graduated inspection glass, located between the conservator and the tank |  |  | Yes |  |
|  | • Device to protect the compartment of the tap changer |  |  | Yes |  |
|  | - Pressure relief valve |  |  | Yes |  |
|  | - Buchholz relay (running on the oil flow) |  |  | Yes |  |
|  | • Pressure relief valve (Qualitrol type) installed on the transformer tank, fitted with a contact status indication on / off |  |  | Yes |  |
|  | 16. Documents to be submitted |  |  |  |  |
|  | • Submital fase |  |  | 3 ex. |  |
|  | - Dimension drawing (MV-drawing) with the list of equipment |  |  |  |  |
|  | - Layout drawing showing the accessories,wheels, the position of the bushing and isolation distances required by the transformer |  |  |  |  |
|  | - List of references |  |  |  |  |
|  | • Ordering fase |  |  | 3 ex. |  |
|  | - instruction manual |  |  |  |  |
|  | - erection instruction manual |  |  |  |  |
|  | - maintenance instruction manual |  |  |  |  |
|  | - drawings |  |  |  |  |
|  | - detailed dimensional drawing |  |  |  |  |
|  | - drawing of the rating plate |  |  |  |  |
|  | - MV diagrams |  |  |  |  |
|  | - drawing of electrical circuits |  |  |  |  |
|  | - schematic with the relative position of the windings respect to the core |  |  |  |  |
|  | - Detailed description of the tap changer |  |  |  |  |
|  | - Description of the surface treatment |  |  |  |  |
|  | - Description of the Buchholz relay |  |  |  |  |
|  | - Description of the oil level indicator |  |  |  |  |
|  | - Description of the relief valve |  |  |  |  |
|  | - Description of the dial thermometer temperature |  |  |  |  |
|  | - Description of the sealing device oil / air |  |  |  |  |
|  | - Description of protection devices |  |  |  |  |
|  | - Routine, factory, on site testing reports of similar equipment |  |  |  |  |
|  | • Completed Manufactuer final report including |  |  | 3 ex. |  |
|  | - instruction manual |  |  |  |  |
|  | - erection instruction manual |  |  |  |  |
|  | - maintenance instruction manual |  |  |  |  |
|  | - as built drawings and diagrams |  |  |  |  |
|  | - Detailed layout drawing |  |  |  |  |
|  | - drawing of the MV cabinets |  |  |  |  |
|  | - as built MV diagrams |  |  |  |  |
|  | - schematic with the position of the windings respect to the core |  |  |  |  |
|  | - Drawing of the rating plate |  |  |  |  |
|  | - Detailed description of accessories |  |  |  |  |
|  | - Standard routine, factory, on site test reports |  |  |  |  |
|  | 17. Languages |  |  |  |  |
|  | • All documents establish in English |  |  | Yes |  |

| TECHNICAL SCHEDULE – Main Data Auxiliary Transformer 6 kV/400V |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Description |  |  | Units | Imposed Values | Guaranteed Values |
|  | 1. General characteristics |  |  |  |  |
|  | • Manufacturer |  |  | Specify |  |
|  | • Type transformer oil immersed |  |  | Yes |  |
|  | • Indoor/Outdoor installation |  |  | Outdoor |  |
|  | • Number of phases |  |  | 3 |  |
|  | • Internal insulation paper and oil |  |  | Yes |  |
|  | • Cooling mode |  |  | ONAN |  |
|  | • Rated frequency (fr) |  | Hz | 50 |  |
|  | 2. Normal service conditions |  |  |  |  |
|  | • Ambient temperature range |  | °C | -35 to +50 |  |
|  | 3. Rated voltages and currents |  |  |  |  |
|  | • Rated voltages |  |  |  |  |
|  | - Primary voltage (MV) |  | kV | 6 |  |
|  | - Secondary voltage (LV) |  | V | 400 |  |
|  | • Rated power |  | kVA | 400 |  |
|  | 4. Vector group |  |  |  |  |
|  | • Vector group |  |  | Dyn5 |  |
|  | 5. Insulation level |  |  |  |  |
|  | • Primary winding |  |  |  |  |
|  | - Rated voltage (Ur) |  | kV | 7,2 |  |
|  | - Power frequency withstant voltage 50 Hz / 1 min (AC) (Ud) |  | kV | 20 |  |
|  | - Lightning impulse withstand voltage 1,2 / 50 μs (Up) |  | kV peak | 60 |  |
|  | • Secondary winding |  |  |  |  |
|  | - Rated voltage (Ur) |  | kV | 1.1 |  |
|  | - Power frequency withstant voltage 50 Hz / 1 min (AC) (Ud) |  | kV | 3 |  |
|  | 6. Tap changer |  |  |  |  |
|  | • Type: off load |  |  | Yes |  |
|  | • Number of positions |  |  | 5 |  |
|  | • Tapping range |  | % | ± 2 x 2,5 |  |
|  | 7. Losses and impedance voltage |  |  |  |  |
|  | • No-load loss |  |  |  |  |
|  | - Value |  | kW | Specify |  |
|  | - Maximum tolerance |  | % | ± 15 |  |
|  | • Load loss at 75°C and rated current (tap 3) |  |  |  |  |
|  | - Value |  | kW | Specify |  |
|  | - Maximum tolerance |  | % | ± 15 |  |
|  | • Short circuit impedance at 75°C and rated current (tap 3) |  |  |  |  |
|  | - Rated value |  | % | 4 |  |
|  | - Maximum tolerance |  | % | ± 10 |  |
|  | 8. Noise Level |  |  |  |  |
|  | • Sound pressure/sound power level (Lw) |  | dB(A) | 62 |  |
|  | • Maximum tolerance |  | dB(A) | 2 |  |

| TECHNICAL SCHEDULE – Data for Information Auxiliary Transformer 6 kV/400V |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Description |  |  | Units | Imposed Values | Guaranteed Values |
|  | 1. General characteristics |  |  |  |  |
|  | • Place of manufacture |  |  | Specify |  |
|  | • Type |  |  | Specify |  |
|  | • Standards |  |  | Acc. to IEC |  |
|  | • Hermetic type with complete filling |  |  |  |  |
|  | • Breathing type with oil conservator |  |  | Yes |  |
|  | 2. Normal service conditions(please refer to the site conditions of each substation) |  |  |  |  |
|  | • Ambient temperature range |  | °C |  |  |
|  | • Relative humidity |  | % |  |  |
|  | • Maximum altitude |  | M |  |  |
|  | • Maximum ice coating |  | mm |  |  |
|  | • Maximum pressure of the wind speed |  | Pa |  |  |
|  | • Solar radiation |  | W/m² |  |  |
|  | 3. Rated voltages and currents |  |  |  |  |
|  | • Rated currents |  |  |  |  |
|  | - Primary current |  | A | Specify |  |
|  | - Secondary current |  | A | Specify |  |
|  | 4. Tap changer |  |  |  |  |
|  | • Manufacturer |  |  | Specify |  |
|  | • Location: between windings and bushings |  |  | Yes |  |
|  | • Tap 1: tap with highest ratio |  |  | Yes |  |
|  | • Padlock possibility |  |  | Yes |  |
|  | 5.Temperature rise |  |  |  |  |
|  | • Maximum temperature rise at rated power (tap 3): |  |  |  |  |
|  | - Top-oil temperature rise |  | K | 60 |  |
|  | - Average winding temperature rise |  | K | 65 |  |
|  | - Winding hot spot rise |  | K | 78 |  |
|  | 6. Bushings (phases & neutral point) |  |  |  |  |
|  | • Primary bushings |  |  |  |  |
|  | - Number |  |  | 3 |  |
|  | - Bushing type (Porcelain/Bolted plug) |  |  | Specify |  |
|  | - Manufacturer |  |  | Specify |  |
|  | - Fabrication type |  |  | Specify |  |
|  | - Insulation levels |  |  |  |  |
|  | . Rated voltage (Ur) |  | kV | 7,2 |  |
|  | . Power frequency withstant voltage 50 Hz / 1 min (AC) - (Ud) |  | kV | 20 |  |
|  | . Lightning impulse withstand voltage 1,2 / 50 μs (Up) |  | kV peak | 60 |  |
|  | - Rated current (Ir) |  | A | 630 |  |
|  | - Connector type for plug-in type (not included in order) |  |  | Specify |  |
|  | • Secondary bushings |  |  |  |  |
|  | - Number |  |  | 4 |  |
|  | - Bushing type (Porcelain/Bolted plug) |  |  | Porcelain |  |
|  | - Manufacturer |  |  | Specify |  |
|  | - Insulation levels |  |  |  |  |
|  | . Rated voltage (Ur) |  | kV | 1.1 |  |
|  | . Power frequency withstant voltage 50 Hz / 1 min (AC) - (Ud) |  | kV | 3 |  |
|  | - Rated current (Ir) |  | A | 630 |  |
|  | - Protected by an air compartment |  |  | Yes |  |
|  | 7. Mechanical characteristics |  |  |  |  |
|  | • Windings |  |  |  |  |
|  | - Winding configuration (round, oval…) |  |  | Specify |  |
|  | - Winding material primary (MV) |  |  | Specify |  |
|  | - Winding material secondary (LV) |  |  | Specify |  |
|  | - Insulation material |  |  | Specify |  |
|  | • Core |  |  |  |  |
|  | - Core material |  |  | Specify |  |
|  | - Specific losses |  |  |  |  |
|  | . At 1,5T |  | W/kg | Specify |  |
|  | . At 1,7T |  | W/kg | Specify |  |
|  | - Maximum inductance at rated voltage |  | T | Specify |  |
|  | • Tank |  |  |  |  |
|  | - Cover: welded or bolted |  |  | Specify |  |
|  | - Lifting lugs: 2 pieces on the cover, hole diameter > 28 mm |  |  | Yes |  |
|  | - Pulling eyes |  |  | Yes |  |
|  | - Earthing bolt on cover, M12 |  |  | Yes |  |
|  | - Earthing bolt on tank bottom, M12 |  |  | Yes |  |
|  | - Oil filling device on cover |  |  | Yes |  |
|  | - Oil drain valve suitable for taking oil samples (type DIN A22 or similar) |  |  | Yes |  |
|  | - Oil conservator |  |  | Yes/No |  |
|  | - Free ground distance |  | mm | 250 |  |
|  | • Wheels |  |  | Yes/No |  |
|  | - Clearance between axes |  | mm | min. 520 |  |
|  | • Rating plate |  |  | Acc. IEC 60076 |  |
|  | - Material |  |  | inox |  |
|  | - Language |  |  | English |  |
|  | 8. Oil characteristics |  |  |  |  |
|  | - Manufacturer |  |  | Specify |  |
|  | - Type of oil |  |  | Specify |  |
|  | - Label |  |  | Specify |  |
|  | - Certificate |  |  | To deliver |  |
|  | 9. Protection of secondary circuits |  |  |  |  |
|  | • Withdrawable (with a crank) tripolar Circuit breaker 400V |  |  | 1 |  |
|  | - Mounted inside the LV cubicle and connected to the LV phases; |  |  | Yes |  |
|  | - Manufacturer |  |  | Specify |  |
|  | - Type |  |  | Specify |  |
|  | - 3 phases and neutral point available inside the enclosure, on a copper bar at the height of the lower circuit breaker connections; |  |  | Yes |  |
|  | - Rated current setting CB "400V" |  | A | 400 |  |
|  | - CB tripg coil (220 VDC) |  |  | Yes |  |
|  | - Auxiliary contacts; |  |  |  |  |
|  | . CB open/closed |  |  | (2NO +2NC) |  |
|  | . CB position in/out |  |  | (1NO +1NC) |  |
|  | - Temporisation relay 0…60 sec |  |  | Yes |  |
|  | - Locking coil EDV - 220Vdc |  |  | Yes |  |
|  | - Push button request racking |  |  | Yes |  |
|  | - Heating resistor with thermostat (230V) |  |  | Yes |  |
|  | - Safety protection for all terminals |  |  | Yes |  |
|  | - Labelled terminals and wires, grouping all contacts of DGPT, circuit breaker, … |  |  | Yes |  |
|  | 10. Weights and dimensions |  |  |  |  |
|  | • Length (including control cabinet) |  | mm | Specify |  |
|  | • Width |  | mm | Specify |  |
|  | • Total height |  | mm | Specify |  |
|  | • Total weight with oil |  | kg | Specify |  |
|  | • Oil weight |  | kg | Specify |  |
|  | • Aluminium weight |  | kg | Specify |  |
|  | • Copper weight |  | kg | Specify |  |
|  | 11. Painting |  |  |  |  |
|  | • Procedure according to GTS (General Specifications) or similar and approved |  |  | GTS / similar |  |
|  | • The transformer and its accessories are guaranteed corrosion-free for 10 years. The environment is corrosive, industrial and salty. The supplier guarantees that the paint procedure complies with this requirement |  |  | Yes |  |
|  | • Total thickness |  |  |  |  |
|  | - If depth of ribs > 150 mm |  | μm | 140 |  |
|  | - If depth of ribs ≤ 150 mm |  | μm | 210 |  |
|  | • Finishing colour (RAL-code) |  |  | Specify |  |
|  | • Anticorrosion protection |  |  | Yes |  |
|  | - type |  |  | hot galvanised |  |
|  | • Bolts, nuts, …are |  |  |  |  |
|  | - In stainless steel for diameters < M16 |  |  | Yes |  |
|  | - For diameters > M16: hot dip galvanised and painted |  |  | Yes |  |
|  | • Metal parts: hot dip galvanised |  |  | Yes |  |
|  | • Earthing connections, metal conductors, … will be free of paint |  |  | Yes |  |
|  | • Lifting lugs, jacking lugs, pulling eyes: red painted |  |  | Yes |  |
|  | 12. Documents to be submitted |  |  |  |  |
|  | • Submital fase |  |  | 3 ex. |  |
|  | - General documentation |  |  |  |  |
|  | - List of references |  |  |  |  |
|  | - Type test reports |  |  |  |  |
|  | - datasheet completed |  |  |  |  |
|  | - indicative dimensional drawing |  |  |  |  |
|  | • Ordering fase |  |  | 3 ex. |  |
|  | - instruction manual |  |  |  |  |
|  | - erection instruction manual |  |  |  |  |
|  | - maintenance instruction manual |  |  |  |  |
|  | - drawings |  |  |  |  |
|  | - detailed dimensional drawing |  |  |  |  |
|  | - drawing of the rating plate |  |  |  |  |
|  | - LV diagrams |  |  |  |  |
|  | - drawing of electrical circuits |  |  |  |  |
|  | • Completed Manufactuer final report including |  |  | 3 ex. |  |
|  | - instruction manual |  |  |  |  |
|  | - erection instruction manual |  |  |  |  |
|  | - maintenance instruction manual |  |  |  |  |
|  | - as built drawings and diagrams |  |  |  |  |
|  | - Standard routine, factory, on site test reports |  |  |  |  |
|  | 13. Languages |  |  |  |  |
|  | • All documents establish in English |  |  | Yes |  |

| TECHNICAL SCHEDULE – Main Data Auxiliary Transformer 10 kV/400V |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Description |  |  | Units | Imposed Values | Guaranteed Values |
|  | 1. General characteristics |  |  |  |  |
|  | • Manufacturer |  |  | Specify |  |
|  | • Type transformer oil immersed |  |  | Yes |  |
|  | • Indoor/Outdoor installation |  |  | Outdoor |  |
|  | • Number of phases |  |  | 3 |  |
|  | • Internal insulation paper and oil |  |  | Yes |  |
|  | • Cooling mode |  |  | ONAN |  |
|  | • Rated frequency (fr) |  | Hz | 50 |  |
|  | 2. Normal service conditions |  |  |  |  |
|  | • Ambient temperature range |  | °C | -35 to +50 |  |
|  | 3. Rated voltages and currents |  |  |  |  |
|  | • Rated voltages |  |  |  |  |
|  | - Primary voltage (MV) |  | kV | 10 |  |
|  | - Secondary voltage (LV) |  | V | 400 |  |
|  | • Rated power |  | kVA | 400 |  |
|  | 4. Vector group |  |  |  |  |
|  | • Vector group |  |  | Dyn5 |  |
|  | 5. Insulation level |  |  |  |  |
|  | • Primary winding |  |  |  |  |
|  | - Rated voltage (Ur) |  | kV | 12 |  |
|  | - Power frequency withstant voltage 50 Hz / 1 min (AC) (Ud) |  | kV | 28 |  |
|  | - Lightning impulse withstand voltage 1,2 / 50 μs (Up) |  | kV peak | 75 |  |
|  | • Secondary winding |  |  |  |  |
|  | - Rated voltage (Ur) |  | kV | 1.1 |  |
|  | - Power frequency withstant voltage 50 Hz / 1 min (AC) (Ud) |  | kV | 3 |  |
|  | 6. Tap changer |  |  |  |  |
|  | • Type: off load |  |  | Yes |  |
|  | • Number of positions |  |  | 5 |  |
|  | • Tapping range |  | % | ± 2 x 2,5 |  |
|  | 7. Losses and impedance voltage |  |  |  |  |
|  | • No-load loss |  |  |  |  |
|  | - Value |  | kW | Specify |  |
|  | - Maximum tolerance |  | % | ± 15 |  |
|  | • Load loss at 75°C and rated current (tap 3) |  |  |  |  |
|  | - Value |  | kW | Specify |  |
|  | - Maximum tolerance |  | % | ± 15 |  |
|  | • Short circuit impedance at 75°C and rated current (tap 3) |  |  |  |  |
|  | - Rated value |  | % | 4 |  |
|  | - Maximum tolerance |  | % | ± 10 |  |
|  | 8. Noise Level |  |  |  |  |
|  | • Sound pressure/sound power level (Lw) |  | dB(A) | 62 |  |
|  | • Maximum tolerance |  | dB(A) | 2 |  |

| TECHNICAL SCHEDULE – Data for Information Auxiliary Transformer 10 kV/400V |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Description |  |  | Units | Imposed Values | Guaranteed Values |
|  | 1. General characteristics |  |  |  |  |
|  | • Place of manufacture |  |  | Specify |  |
|  | • Type |  |  | Specify |  |
|  | • Standards |  |  | Acc. to IEC |  |
|  | • Hermetic type with complete filling |  |  |  |  |
|  | • Breathing type with oil conservator |  |  | Yes |  |
|  | 2. Normal service conditions(please refer to the site conditions of each substation) |  |  |  |  |
|  | • Ambient temperature range |  | °C |  |  |
|  | • Relative humidity |  | % |  |  |
|  | • Maximum altitude |  | m |  |  |
|  | • Maximum ice coating |  | mm |  |  |
|  | • Maximum pressure of the wind speed |  | Pa |  |  |
|  | • Solar radiation |  | W/m² |  |  |
|  | 3. Rated voltages and currents |  |  |  |  |
|  | • Rated currents |  |  |  |  |
|  | - Primary current |  | A | Specify |  |
|  | - Secondary current |  | A | Specify |  |
|  | 4. Tap changer |  |  |  |  |
|  | • Manufacturer |  |  | Specify |  |
|  | • Location: between windings and bushings |  |  | Yes |  |
|  | • Tap 1: tap with highest ratio |  |  | Yes |  |
|  | • Padlock possibility |  |  | Yes |  |
|  | 5.Temperature rise |  |  |  |  |
|  | • Maximum temperature rise at rated power (tap 3): |  |  |  |  |
|  | - Top-oil temperature rise |  | K | 60 |  |
|  | - Average winding temperature rise |  | K | 65 |  |
|  | - Winding hot spot rise |  | K | 78 |  |
|  | 6. Bushings (phases & neutral point) |  |  |  |  |
|  | • Primary bushings |  |  |  |  |
|  | - Number |  |  | 3 |  |
|  | - Bushing type (Porcelain/Bolted plug) |  |  | Specify |  |
|  | - Manufacturer |  |  | Specify |  |
|  | - Fabrication type |  |  | Specify |  |
|  | - Insulation levels |  |  |  |  |
|  | . Rated voltage (Ur) |  | kV | 12 |  |
|  | . Power frequency withstant voltage 50 Hz / 1 min (AC) - (Ud) |  | kV | 28 |  |
|  | . Lightning impulse withstand voltage 1,2 / 50 μs (Up) |  | kV peak | 75 |  |
|  | - Rated current (Ir) |  | A | 630 |  |
|  | - Connector type for plug-in type (not included in order) |  |  | Specify |  |
|  | • Secondary bushings |  |  |  |  |
|  | - Number |  |  | 4 |  |
|  | - Bushing type (Porcelain/Bolted plug) |  |  | Porcelain |  |
|  | - Manufacturer |  |  | Specify |  |
|  | - Insulation levels |  |  |  |  |
|  | . Rated voltage (Ur) |  | kV | 1.1 |  |
|  | . Power frequency withstant voltage 50 Hz / 1 min (AC) - (Ud) |  | kV | 3 |  |
|  | - Rated current (Ir) |  | A | 630 |  |
|  | - Protected by an air compartment |  |  | Yes |  |
|  | 7. Mechanical characteristics |  |  |  |  |
|  | • Windings |  |  |  |  |
|  | - Winding configuration (round, oval…) |  |  | Specify |  |
|  | - Winding material primary (MV) |  |  | Specify |  |
|  | - Winding material secondary (LV) |  |  | Specify |  |
|  | - Insulation material |  |  | Specify |  |
|  | • Core |  |  |  |  |
|  | - Core material |  |  | Specify |  |
|  | - Specific losses |  |  |  |  |
|  | . At 1,5T |  | W/kg | Specify |  |
|  | . At 1,7T |  | W/kg | Specify |  |
|  | - Maximum inductance at rated voltage |  | T | Specify |  |
|  | • Tank |  |  |  |  |
|  | - Cover: welded or bolted |  |  | Specify |  |
|  | - Lifting lugs: 2 pieces on the cover, hole diameter > 28 mm |  |  | Yes |  |
|  | - Pulling eyes |  |  | Yes |  |
|  | - Earthing bolt on cover, M12 |  |  | Yes |  |
|  | - Earthing bolt on tank bottom, M12 |  |  | Yes |  |
|  | - Oil filling device on cover |  |  | Yes |  |
|  | - Oil drain valve suitable for taking oil samples (type DIN A22 or similar) |  |  | Yes |  |
|  | - Oil conservator |  |  | Yes/No |  |
|  | - Free ground distance |  | mm | 250 |  |
|  | • Wheels |  |  | Yes/No |  |
|  | - Clearance between axes |  | mm | min. 520 |  |
|  | • Rating plate |  |  | Acc. IEC 60076 |  |
|  | - Material |  |  | inox |  |
|  | - Language |  |  | English |  |
|  | 8. Oil characteristics |  |  |  |  |
|  | - Manufacturer |  |  | Specify |  |
|  | - Type of oil |  |  | Specify |  |
|  | - Label |  |  | Specify |  |
|  | - Certificate |  |  | To deliver |  |
|  | 9. Protection of secondary circuits |  |  |  |  |
|  | • Withdrawable (with a crank) tripolar Circuit breaker 400V |  |  | 1 |  |
|  | - Mounted inside the LV cubicle and connected to the LV phases; |  |  | Yes |  |
|  | - Manufacturer |  |  | Specify |  |
|  | - Type |  |  | Specify |  |
|  | - 3 phases and neutral point available inside the enclosure, on a copper bar at the height of the lower circuit breaker connections; |  |  | Yes |  |
|  | - Rated current setting CB "400V" |  | A | 400 |  |
|  | - CB tripg coil (220 VDC) |  |  | Yes |  |
|  | - Auxiliary contacts; |  |  |  |  |
|  | . CB open/closed |  |  | (2NO +2NC) |  |
|  | . CB position in/out |  |  | (1NO +1NC) |  |
|  | - Temporisation relay 0…60 sec |  |  | Yes |  |
|  | - Locking coil EDV - 220Vdc |  |  | Yes |  |
|  | - Push button request racking |  |  | Yes |  |
|  | - Heating resistor with thermostat (230V) |  |  | Yes |  |
|  | - Safety protection for all terminals |  |  | Yes |  |
|  | - Labelled terminals and wires, grouping all contacts of DGPT, circuit breaker, … |  |  | Yes |  |
|  | 10. Weights and dimensions |  |  |  |  |
|  | • Length (including control cabinet) |  | mm | Specify |  |
|  | • Width |  | mm | Specify |  |
|  | • Total height |  | mm | Specify |  |
|  | • Total weight with oil |  | kg | Specify |  |
|  | • Oil weight |  | kg | Specify |  |
|  | • Aluminium weight |  | kg | Specify |  |
|  | • Copper weight |  | kg | Specify |  |
|  | 11. Painting |  |  |  |  |
|  | • Procedure according to GTS (General Specifications) or similar and approved |  |  | GTS / similar |  |
|  | • The transformer and its accessories are guaranteed corrosion-free for 10 years. The environment is corrosive, industrial and salty. The supplier guarantees that the paint procedure complies with this requirement |  |  | Yes |  |
|  | • Total thickness |  |  |  |  |
|  | - If depth of ribs > 150 mm |  | μm | 140 |  |
|  | - If depth of ribs ≤ 150 mm |  | μm | 210 |  |
|  | • Finishing colour (RAL-code) |  |  | Specify |  |
|  | • Anticorrosion protection |  |  | Yes |  |
|  | - type |  |  | hot galvanised |  |
|  | • Bolts, nuts, …are |  |  |  |  |
|  | - In stainless steel for diameters < M16 |  |  | Yes |  |
|  | - For diameters > M16: hot dip galvanised and painted |  |  | Yes |  |
|  | • Metal parts: hot dip galvanised |  |  | Yes |  |
|  | • Earthing connections, metal conductors, … will be free of paint |  |  | Yes |  |
|  | • Lifting lugs, jacking lugs, pulling eyes: red painted |  |  | Yes |  |
|  | 12. Documents to be submitted |  |  |  |  |
|  | • Submital fase |  |  | 3 ex. |  |
|  | - General documentation |  |  |  |  |
|  | - List of references |  |  |  |  |
|  | - Type test reports |  |  |  |  |
|  | - datasheet completed |  |  |  |  |
|  | - indicative dimensional drawing |  |  |  |  |
|  | • Ordering fase |  |  | 3 ex. |  |
|  | - instruction manual |  |  |  |  |
|  | - erection instruction manual |  |  |  |  |
|  | - maintenance instruction manual |  |  |  |  |
|  | - drawings |  |  |  |  |
|  | - detailed dimensional drawing |  |  |  |  |
|  | - drawing of the rating plate |  |  |  |  |
|  | - LV diagrams |  |  |  |  |
|  | - drawing of electrical circuits |  |  |  |  |
|  | • Completed Manufactuer final report including |  |  | 3 ex. |  |
|  | - instruction manual |  |  |  |  |
|  | - erection instruction manual |  |  |  |  |
|  | - maintenance instruction manual |  |  |  |  |
|  | - as built drawings and diagrams |  |  |  |  |
|  | - Standard routine, factory, on site test reports |  |  |  |  |
|  | 13. Languages |  |  |  |  |
|  | • All documents establish in English |  |  | Yes |  |