## Лист1
Clarification
ELC:
1. P299 1.1.3.3.4. Outdoor 110 kV substation：
one (1) busbar measurement bay，but the drawing of signle line diagram have two(2) measurement bay。 | Each busbar should have one (1) measurement bay
2. Provide the technical schedules of protection equipment. | The requirements to protection equipment is mentioned on the pages 884-913
3. Provide the technical schedules of 10kV current limiting reactor. | Attached it is sending
4.In page 308 .335 .360 .390 “Only worldwide well known Manufacturers are accepted. The selection of any other Manufacturer will be submitted to Employer's approval.”please clarify what manufacturers can be accepted?
5.In page310.392 “The transmission of the information to the new substation to the Dispatching will use the CEI 60870-5-104 protocol ” according to other paragraphs it is use IEC.Please clarify . | The transmission of the information to the Dispatching center will use the IEC 60870-5-104 protocol
6.Please provide the exact dimensions of existing 10kV building for all substation. | Attached we send you copies of substation plans
7.Please confirm that if the existing gantries in substation could be used again in this project . | As per items mentioned in Particular specifications
Civil：
1. Whether all the structure calculation can be calculated in accordance with the norms and standards. | Yes
2. Need to change the first phase structure of the equipment bracket height and the size of the base can provide. | We ask you to clarify the question
3. The existing building structure, building height, and building area can provide. | Attached we send you copies of substation plans
4. The expansion is land requisition procedures needed. | No
5. Station toilet is indoor or dry. | They are indoor
Telecommunication：
1.Please define the scope of telecommunication work about the four substations of this project clearly. | We will inform you latter
2.Please provide the figure of grid telecommunication status quo related to this project. | We will inform you latter
3.Provide the existing drawing of power line carrier channels and fiber optic communication channels in four substations of this project, including model of power line carrier equipment，SDH equipment and PCM Access multiplexers. | We will inform you latter
4.Provide the technical schedules of telecommunication equipment. | We will inform you latter