| TECHNICAL SCHEDULE – Main Data |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| 10 kV Power Reactor – 40MVA |  |  |  |  |  |
| Description |  |  | Units | Imposed Values | Guaranteed Values |
| 1 | General characteristics |  |  |  |  |
|  | • Concrete one-phase unit |  |  | Yes |  |
|  | • Indoor/Outdoor installation |  |  | Indoor |  |
|  | • Frequency |  | Hz | 50 |  |
|  | • Number of windings per phase |  |  | 1 |  |
|  | • Phases layout |  |  | Horizontal |  |
| 2 | Normal service conditions |  |  |  |  |
|  | • Ambient temperature range |  | °C | -35 to +50 |  |
| 3 | Rated power, temperature rise and overload |  |  |  |  |
|  | • Cooling mode |  |  | ONAN |  |
| 4 | Rated inductive reactance value |  | Ohm | 0.2 |  |
|  | Tolerance |  | % /phase | 0-15 |  |
| 5 | Rated current |  | A | 2500 |  |
| 6 | Insulation levels |  |  |  |  |
|  | • Windings: |  |  |  |  |
|  | - Um: highest voltage for equipment |  | kV | 12 |  |
|  | - AC: Rated short duration power frequency withstand voltage |  | kV | 28 |  |
|  | - LI: Rated impulse withstand voltage |  | kV peak | 75 |  |
|  | • Partial discharges: Measurements acc. to IEC 60076-3 |  | Yes | Yes |  |
| 7 | Exceptional service conditions |  |  |  |  |
|  | • Short-circuit withstand capability of the windings |  | kA | 60 |  |
|  | • Maximum short-circuit duration |  | s | 3 |  |
|  | • Possible permanent over-voltage |  | % | + 10% |  |
|  | • Harmonic content of load |  |  | Acc. IEC |  |
| 8 | Loses |  |  |  |  |
|  | Lose on one phase |  | kW | ≤14,0 |  |
|  |  |  | % | 15 |  |
| 9. | Diameter of concrete |  | m | ≤2,0 |  |
| 10. | Height of phase |  | m | ≤1,5 |  |